2025 ILLINOIS COMMERCIAL STRETCH ENERGY CODE – DRAFT

1-14-25

AMENDMENTS TO THE 2024 IECC 1st Printing

New text added by Illinois amendment to the 2024 IECC

~~Deleted text removed by Illinois amendment to the 2024 IECC.~~

## IECC—COMMERCIAL PROVISIONS

### CONTENTS

CHAPTER 1—SCOPE AND ADMINISTRATION 18

C101—Scope and General Requirements 18

C102—Applicability 18

C103—Code Compliance Agency. 19

C104—Alternative Materials, Design and Methods of Construction and Equipment 19

C105—Construction Documents 19

C106—Fees 21

C107—Inspections 21

C108—Notice of Approval 22

C109—Means of Appeals 22

C110—Stop Work Order 22

CHAPTER 2—DEFINITIONS 23

C201—General 23

C202—General Definitions 23

CHAPTER 3—GENERAL REQUIREMENTS. 33

C301—Climate Zones 33

C302—Design Conditions 66

C303—Materials, Systems and Equipment 66

CHAPTER 4—COMMERCIAL ENERGY EFFICIENCY 68

C401—General 68

C402—Building Thermal Envelope Requirements 68

C403—Building Mechanical Systems 86

C404 —Service Water Heating 131

C405 —Electrical Power and Lighting Systems 138

C406—Additional Efficiency, Renewable and Load Management Requirements 160

C407—Simulated Building Performance 191

C408 —Maintenance Information and System Commissioning. 200

C409—Calculation of the HVAC Total System

Performance Ratio 205

CHAPTER 5—EXISTING BUILDINGS 221

C501—General 221

C502—Additions 221

C503—Alterations 222

C504—Repairs 225

C505—Change of Occupancy or Use 226

CHAPTER 6—REFERENCED STANDARDS 227

APPENDIX CA BOARD OF APPEALS—COMMERCIAL 235

CA101—General 235

APPENDIX CB SOLAR-READY ZONE—COMMERCIAL 237

CB101—Scope 237

CB102—General Definition 237

CB103—Solar-Ready Zone 237

APPENDIX CC ZERO ENERGY COMMERCIAL BUILDING PROVISIONS 238

CC101—General 238

CC102—Definitions 238

CC103—Minimum Renewable Energy 239

APPENDIX CD THE 2030 GLIDE PATH 241

CD101—Compliance 241

APPENDIX CE REQUIRED HVAC TOTAL SYSTEM PERFORMANCE RATIO (TSPR) 243

CE101—General 243

APPENDIX CF ENERGY CREDITS 244

CF101—General 244

CF102—Advanced Energy Credit Package 244

CF103—Buildings Without Heat Pumps 245

CF104—Existing Buildings 245

APPENDIX CG ELECTRIC VEHICLE CHARGING INFRASTRUCTURE 246

CG101—Electric Vehicle Power Transfer 246

CG102—Referenced Standards 248

APPENDIX CH ELECTRIC-READY COMMERCIAL BUILDING PROVISIONS 249

CH101—General 249

CH102—Definitions 249

CH103—New Commercial Building 249

APPENDIX CI DEMAND RESPONSIVE CONTROLS 253

CI101—Demand Responsive Heating and Cooling

Systems 253

CI102—Demand Responsive Water Heating 253

CI103—Demand Responsive Lighting Controls 254

CI104—Referenced Standards 254

APPENDIX CJ ELECTRICAL ENERGY STORAGE SYSTEM 255

CJ101—Electrical Energy Storage System 255

CJ102—Referenced Standards 255

**APPENDIX CK TOTAL BUILDING PERFORMANCE PATHWAY**

CK101—Scope

CK102—Compliance Based on Site Energy

INDEX 256

RESOURCE CRA ALL-ELECTRIC COMMERCIAL BUILDING PROVISIONS 262

CRA101—General 262

CRA102—Definitions 262

CRA103—New Commercial Buildings 262

CRA104—Existing Commercial Buildings 263

CRA105—Referenced Standards 264

RESOURCE CRB THE 2030 GLIDE PATH

(PRESCRIPTIVE) 265

CRB101—Compliance 265

### SCOPE AND ADMINISTRATION



CHAPTER

**1** [CE]

**User notes:**

***About this chapter:*** *Chapter 1 establishes the limits of applicability of the code and describes how the code is to be applied and enforced. Chapter 1 is in two parts: Part 1—Scope and Application and Part 2—Administration and Enforcement. Section C101 identifies what buildings, systems, appliances and equipment fall under its purview and references other I-Codes as applicable. Standards and codes are scoped to the extent referenced.*

*The code is intended to be adopted as a legally enforceable document and it cannot be effective without adequate provisions for its administration and enforcement. The provisions of Chapter 1 establish the authority and duties of the code official appointed by the authority having jurisdiction and also establish the rights and privileges of the design professional, contractor and property owner.*

***QR code use:*** *A QR code is placed at the beginning of any section that has undergone technical revision. To see those revisions, scan the QR code with a smart device or enter the 7-digit code beneath the QR code at the end of the following URL: qr.iccsafe.org/ (see Formatting Changes to the 2024 International Codes for more information).*

***PART 1—SCOPE AND APPLICATION***

SECTION C101—SCOPE AND GENERAL REQUIREMENTS

**C101.1 Title.** This code shall be known as the *2025 Illinois Commercial Stretch* *Energy ~~Conservation~~ Code* ~~of~~ **~~[NAME OF JURISDICTION]~~** and shall mean: ~~be cited as such. It is referred to herein as “this code.”~~

With respect to the State facilities covered by 71 Ill. Adm. Code 600 Subpart B:

This Part, all additional requirements incorporated within Subpart B (including the 2024 *International Energy Conservation* *Code* Commercial Provisions, including all published errata but excluding published supplements that encompass ASHRAE 90.1-2022) and any statutorily authorized adaptations to the incorporated standards adopted by CDB are effective xxxx.

With respect to the privately funded commercial facilities covered by 71 Ill. Adm. Code 600 Subpart C:

This Part, all additional requirements incorporated within Subpart C (including the 2024 *International Energy Conservation*

*Code* Commercial Provisions, including all published errata and excluding published supplements that encompass ASHRAE 90.1-2022) and any statutorily authorized adaptations to the incorporated standards adopted by CDB is effective upon adoption by a Municipality and takes the place of the *Illinois Energy* *Conservation Code* with respect to commercial buildings.

No unit of local government, including any home rule unit, may regulate energy-efficient building standards for commercial buildings in a manner that is less stringent than the standards established pursuant to this *Illinois Commercial* *Stretch Energy Code.*

**C101.1.1 Adoption.** The Board shall adopt amendments to this code and include site energy index standards as

established in the Energy Efficient Building Act [20 ILCS 3125/55] as follows:

By June 30, 2024, with a site energy index no greater than 0.60 of the 2006 IECC.

By December 31, 2025, with a site energy index no greater than 0.50 of the 2006 IECC.

By December 31, 2028, with a site energy index no greater than 0.44 of the 2006 IECC.

By December 31, 2031, with a site energy index no greater than 0.39 of the 2006 IECC.

**C101.2 Scope.** This code applies to the design and construction of buildings not covered by the scope of the IECC—Residential Provisions.

**C101.2.1 Appendices.** Provisions in the appendices shall not apply unless specifically adopted. Appendices CG, CI, CJ, and CK are hereby adopted into the *Illinois Commercial Stretch Energy Code.*

**C101.3 Intent.** The IECC—Commercial Provisions provide market-driven, enforceable requirements for the design and construction of *commercial buildings*, providing minimum efficiency requirements for buildings that result in the maximum level of energy efficiency that is safe, technologically feasible, and life cycle cost effective, considering economic feasibility, including potential costs and savings for consumers and building owners, and

return on investment. Additionally, the code provides jurisdictions with supplemental requirements, including ASHRAE 90.1, and optional requirements that lead to achievement of zero energy buildings, presently, and through glidepaths that achieve zero energy buildings by 2030 and on additional timelines sought by governments, and achievement of additional policy goals as identified by the Energy and Carbon Advisory Council and approved by the Board of Directors. Requirements contained in the code will include, but not be limited to, prescriptive- and performance-based pathways. The code may include nonmandatory appendices incorporat- ing additional energy efficiency and greenhouse gas reduction resources developed by the International Code Council and others. The code will aim to simplify code requirements to facilitate the code’s use and compliance rate. The code is updated on a 3-year cycle with each subsequent edition providing increased energy savings over the prior edition. This code is intended to provide flexi- bility to permit the use of innovative approaches and techniques to achieve this intent. This code is not intended to abridge safety, health or environmental requirements contained in other applicable codes or ordinances.

**C101.4 Compliance.** *~~Residential buildings~~* ~~shall meet the provisions of~~ ~~IECC—Residential Provisions~~. *Commercial buildings* shall meet the provisions of ~~IECC—Commercial Provisions~~ the *Illinois Commercial Stretch Energy Code* covered by 71 Ill. Adm. Code 600 Subpart C. The localauthority having jurisdiction (AHJ) shall establish its own procedures for enforcement of the *Illinois Commercial Stretch Energy Code*. Minimum compliance shall be demonstrated by submission of:

**C101.4.1 Compliance materials.** The *code official* shall be permitted to approve specific computer software, worksheets, compliance manuals and other similar materials that meet the intent of this code; or

**C101.4.2 Professional seals.** The seal of the architect/ engineer as required by Section 14 of the Illinois Architectural Practice Act [225 ILCS 305], Section 12 of the Structural Engineering Licensing Act [225 ILCS 340] and Section 14 of the Illinois Professional Engineering Practice Act [225 ILCS 325]; or

**C101.4.3 COMcheck**TM**.** Compliance certificates generated by the US Department of Energy’s COMcheckTM code compliance tool.

SECTION C102—APPLICABILITY

**C102.1 Applicability.** Where, in any specific case, different sections of this code specify different materials, methods of construction or other requirements, the most restrictive shall govern. Where there is a conflict between a general requirement and a specific requirement, the specific requirement shall govern.

**C102.1.1 Mixed residential and commercial buildings.** Where a *building* includes both *residential building* and *commercial building* portions, each portion shall be separately considered and meet the applicable provisions of ~~IECC—Commercial Provisions or IECC—Residential Provisions~~ the *Illinois Commercial Stretch Energy Code* or the *Illinois Residential Stretch Energy Code.*

**C102.2 Other laws.** The provisions of this code shall not be deemed to nullify any provisions of local, state or federal law.

**C102.3 Applications of references.** References to chapter or section numbers, or to provisions not specifically identified by number, shall be construed to refer to such chapter, section or provision of this code.

**C102.4 Referenced codes and standards.** The codes and standards referenced in this code shall be those listed in Chapter 6, and such codes and standards shall be considered as part of the requirements of this code to the prescribed extent of each such refer- ence and as further regulated in Sections C102.4.1 and C102.4.2.

**C102.4.1 Conflicts.** Where conflicts occur between provisions of this code and referenced codes and standards, the provisions of this code shall apply.

**C102.4.2 Provisions in referenced codes and standards.** Where the extent of the reference to a referenced code or standard includes subject matter that is within the scope of this code, the provisions of this code, as applicable, shall take precedence over the provisions in the referenced code or standard.

**C102.5 Partial invalidity.** If a portion of this code is held to be illegal or void, such a decision shall not affect the validity of the remainder of this code.

***PART 2—ADMINISTRATION AND ENFORCEMENT***

SECTION C103—CODE COMPLIANCE AGENCY

**C103.1 Creation of enforcement agency.** The **[INSERT NAME OF DEPARTMENT]** is hereby created and the official in charge thereof shall be known as the authority having jurisdiction (AHJ). The function of the agency shall be the implementation, administration and enforcement of the provisions of this code.

**C103.2 Appointment.** The AHJ shall be appointed by the chief appointing authority of the jurisdiction.

**C103.3 Deputies.** In accordance with the prescribed procedures of this jurisdiction and with the concurrence of the appointing authority, the AHJ shall have the authority to appoint a deputy AHJ, other related technical officers, inspectors and other employees. Such employees shall have powers as delegated by the AHJ.

SECTION C104—ALTERNATIVE MATERIALS, DESIGN AND METHODS OF CONSTRUCTION AND EQUIPMENT

**C104.1 General.** The provisions of this code are not intended to prevent the installation of any material or to prohibit any design or method of construction not specifically prescribed by this code, provided that any such alternative has been *approved*. The *code offi- cial* shall have the authority to approve an alternative material, design or method of construction upon the written application of the *owner* or the owner’s authorized agent. The *code official* shall first find that the proposed design is satisfactory and complies with the intent of the provisions of this code, and that the material, method or work offered is, for the purpose intended, not less than the equivalent of that prescribed in this code in quality, strength, effectiveness, *fire resistance*, durability, energy conservation and safety. The *code official* shall respond to the applicant, in writing, stating the reasons why the alternative was *approved* or was not *approved*.

**C104.1.1 Above code programs.** Buildings certified in compliance with Passive House Institute (PHI) or Passive House Institute US (PHIUS) programs or buildings that comply with Appendix CC shall be deemed to meet the requirements of this code where such buildings also meet the requirements identified in Table C407.2(1).~~The~~ *~~code official~~* ~~or other authority having jurisdiction shall be permitted to deem a national, state or local energy efficiency program as exceeding the energy efficiency required by this code. Buildings~~ *~~approved~~* ~~in writing by such an energy efficiency program shall be considered to be in compliance with this code~~. ~~The requirements identified in Table C407.2(1) shall be met~~.

SECTION C105—CONSTRUCTION DOCUMENTS

**C105.1 General.** *Construction documents* and other supporting data shall be submitted in one or more sets, or in a digital format where allowed by the *code official*, with each application for a permit. The *construction docu- ments* shall be prepared by a *registered design professional* where required by the statutes of the jurisdiction in which the project is to be constructed. Where special conditions exist, the *code official* is authorized to require necessary *construction documents* to be prepared by a *registered design professional*.

**Exception:** The *code official* is authorized to waive the requirements for *construction documents* or other supporting data if the *code official* determines they are not necessary to confirm compliance with this code.

**C105.2 Information on construction documents.** *Construction documents* shall be drawn to scale on suitable material. Electronic media documents are permitted to be submitted where *approved* by the *code official*.

*Construction documents* shall be of sufficient clarity to indicate the location, nature and extent of the work

proposed, and show in sufficient detail pertinent data and features of the *building*, systems and equipment as herein governed. Details shall include, but are not limited to, the following as applicable:

1. Energy compliance path.
2. Insulation materials and their *R*-values.
3. Fenestration *U-factors* and solar heat gain coefficients (SHGC).
4. Area-weighted *U-factor* and *solar heat gain coefficient* (SHGC) calculations.
5. *Air barrier* and air sealing details, including the location of the *air barrier*.
6. *Thermal bridges* as identified in Section C402.7.
7. Mechanical system design criteria.
8. Mechanical and service water-heating systems and equipment types, sizes and efficiencies.
9. Economizer description.
10. Equipment and system controls.
11. Fan motor horsepower (hp) and controls.
12. Duct sealing, *duct* and pipe insulation and location.
13. Lighting fixture schedule with wattage and control narrative.
14. Location of *daylight* zones on floor plans.
15. Location of pathways for routing of raceways or cable from the on-site renewable energy system to the electrical distribu- tion equipment.
16. Location reserved for inverters, metering equipment and energy storage systems (ESS), and a pathway reserved for routing of raceways or conduit from the renewable energy system to the point of interconnection with the electrical service and the ESS.
17. Location and layout of a designated area for ESS.
18. Rated energy capacity and rated power capacity of the installed or planned ESS.

**C105.2.1 Building thermal envelope depiction.** The *building thermal envelope* shall be represented on the construction drawings.

**C105.2.2 Electrification system.** The construction documents shall provide details for additional electric infrastructure,

including branch circuits, conduit, prewiring, panel capacity, and electrical service capacity, as well as interior and exterior spaces designated for future electric equipment in compliance with the provisions of this code.

**C105.3 Examination of documents.** The *code official* shall examine or cause to be examined the accompanying *construction docu- ments* and shall ascertain whether the construction indicated and described is in accordance with the requirements of this code and other pertinent laws or ordinances. The *code official* is authorized to utilize a *registered design professional*, or other *approved* entity not affiliated with the building design or construction, in conducting the review of the plans and specifications for compliance with the code.

**C105.3.1 Approval of construction documents.** When the *code official* issues a permit where *construction documents* are required, the *construction documents* shall be endorsed in writing and stamped “Reviewed for Code Compliance.” Such *approved construction documents* shall not be changed, modified or altered without authorization from the *code official*. Work shall be done in accordance with the *approved construction documents*.

One set of *construction documents* so reviewed shall be retained by the *code official*. The other set shall be returned to the applicant, kept at the site of work and shall be open to inspection by the *code official* or a duly authorized representative.

**C105.3.2 Previous approvals.** This code shall not require changes in the *construction documents*, construction or designated occupancy of a structure for which a lawful permit has been heretofore issued or otherwise lawfully authorized, and the construc- tion of which has been pursued in good faith within 180 days after the effective date of this code and has not been abandoned.

**C105.3.3 Phased approval.** The *code official* shall have the authority to issue a permit for the construction of part of an energy conservation system before the *construction documents* for the entire system have been submitted or *approved*, provided that adequate information and detailed statements have been filed complying with all pertinent requirements of this code. The hold- ers of such permit shall proceed at their own risk without assurance that the permit for the entire energy conservation system will be granted.

**C105.4 Amended construction documents.** Changes made during construction that are not in compliance with the *approved construction documents* shall be resubmitted for approval as an amended set of *construction documents*.

**C105.5 Retention of construction documents.** One set of *approved construction documents* shall be retained by the *code official* for a period of not less than 180 days from date of completion of the permitted work, or as required by state or local laws.

**C105.6 Building documentation and closeout submittal requirements.** The *construction documents* shall specify that the docu- ments described in this section be provided to the building *owner* or owner’s authorized agent within 90 days of the date of receipt of the certificate of occupancy.

**C105.6.1 Record documents.** *Construction documents* shall be updated to convey a record of the completed work. Such updates shall include mechanical, electrical and control drawings that indicate all changes to size, type and location of components, equipment and assemblies.

**C105.6.2 Compliance documentation.** Energy code compliance documentation and supporting calculations shall be delivered in one document to the building *owner* as part of the project record documents or manuals, or as a standalone document. This document shall include the specific energy code edition utilized for compliance determination for each system, documentation demonstrating compliance with Section C303.1.3 for each fenestration product installed, and the interior lighting power compli- ance path, building area or space-by-space, used to calculate the lighting power allowance.

For projects complying with Item 2 of Section C401.2, the documentation shall include:

* 1. The envelope insulation compliance path.
  2. All compliance calculations including those required by Sections C402.1.4, C403.8.1, C405.3 and C405.5.
  3. A plan for annual energy use data gathering and disclosure as specified in Section C405.13.

For projects complying with Section C407, the documentation shall include that required by Sections C407.3.1 and C407.3.2.

**C105.6.3 Systems operation control.** Training shall be provided to those responsible for maintaining and operating equipment included in the manuals required by Section C105.6.2.

The training shall include:

1. Review of manuals and permanent certificate.
2. Hands-on demonstration of all normal maintenance procedures, normal operating modes, and all emergency shutdown and startup procedures.
3. Training completion report.

SECTION C106—FEES

**C106.1 Fees.** A permit shall not be valid until the fees prescribed by law have been paid. Nor shall an amendment to a permit be released until the additional fee, if any, has been paid.

**C106.2 Schedule of permit fees.** A fee for each permit shall be paid as required, in accordance with the schedule as established by the applicable governing authority.

**C106.3 Valuation of work.** The applicant for a permit shall provide an estimated value of the work for which the permit is being issued at the time of application. Such estimated valuations shall include the total value of the work, including materials and labor. Where, in the opinion of the *code official*, the valuation is underestimated, the permit shall be denied unless the applicant can show detailed estimates acceptable to the *code official*. The final valuation shall be *approved* by the *code official*.

**C106.4 Work commencing before permit issuance.** Any person who commences any work before obtaining the necessary permits shall be subject to a fee established by the *code official* that shall be in addition to the required permit fees.

**C106.5 Related fees.** The payment of the fee for the construction, *alteration*, removal or demolition of work done in connection to or concurrently with the work or activity authorized by a permit shall not relieve the applicant or holder of the permit from the payment of other fees that are prescribed by law.

**C106.6 Refunds.** The *code official* is authorized to establish a refund policy.

SECTION C107—INSPECTIONS

**C107.1 General.** Construction or work for which a permit is required shall be subject to inspection by the *code official*, his or her designated agent or an *approved agency*, and such construction or work shall remain visible and able to be accessed for inspection purposes until *approved*. Approval as a result of an inspection shall not be construed to be an approval of a violation of the provisions of this code or of other ordinances of the jurisdiction. Inspections presuming to give authority to violate or cancel the provisions of this code or of other ordinances of the jurisdiction shall not be valid. It shall be the duty of the permit applicant to cause the work to remain visible and able to be accessed for inspection purposes. Neither the *code official* nor the jurisdiction shall be liable for expense entailed in the removal or replacement of any material, product, system or building component required to allow inspection to validate compliance with this code.

**C107.2 Required inspections.** The *code official*, his or her designated agent or an *approved agency*, upon notification, shall make the inspections set forth in Sections C107.2.1 through C107.2.6.

**C107.2.1 Footing and foundation insulation.** Inspections shall verify the footing and foundation insulation *R-value*, location, thickness, depth of burial and protection of insulation as required by the code, *approved* plans and specifications.

**C107.2.2 Building thermal envelope.** Inspections shall verify the type of insulation, *R*-values, location of insulation, *thermal bridge* mitigation, *fenestration*, *U-factor*, SHGC and VT, and that *air leakage* controls are installed, as required by the code, *approved* plans and specifications.

**C107.2.3 Plumbing system.** Inspections shall verify the type of insulation, *R*-values, protection required, controls and *heat traps*

as required by the code, *approved* plans and specifications.

**C107.2.4 Mechanical system.** Inspections shall verify the installed HVAC equipment for the type and size, controls, insulation, *R*- values, system and damper *air leakage*, minimum fan efficiency, energy recovery and economizer as required by the code, *approved* plans and specifications.

**C107.2.5 Electrical system.** Inspections shall verify lighting system controls, components, ~~and~~ meters, and electric infrastructure as required by the code, *approved* plans and specifications. Where an ESS area is required, inspections shall verify space availability and pathways to electrical service.

**C107.2.6 Final inspection.** The final inspection shall include verification of the installation and proper operation of all required building controls, and documentation verifying activities associated with required *building commissioning* have been conducted in accordance with Section C408.

**C107.3 Reinspection.** A *building* shall be reinspected where determined necessary by the *code official*.

**C107.4 Approved inspection agencies.** The *code official* is authorized to accept reports of third-party inspection agencies not affili- ated with the building design or construction, provided that such agencies are *approved* as to qualifications and reliability relevant to the building components and systems that they are inspecting.

**C107.5 Inspection requests.** It shall be the duty of the holder of the permit or their duly authorized agent to notify the *code official* when work is ready for inspection. It shall be the duty of the permit holder to provide *access* to and means for inspections of such work that are required by this code.

**C107.6 Reinspection and testing.** Where any work or installation does not pass an initial test or inspection, the necessary correc- tions shall be made to achieve compliance with this code. The work or installation shall then be resubmitted to the *code official* for inspection and testing.

SECTION C108—NOTICE OF APPROVAL

**C108.1 Approval.** After the prescribed tests and inspections indicate that the work complies in all respects with this code, a notice of approval shall be issued by the *code official*.

**C108.2 Revocation.** The *code official* is authorized to suspend or revoke, in writing, a notice of approval issued under the provisions of this code wherever the certificate is issued in error, or on the basis of incorrect information supplied, or where it is determined that the *building* or structure, premise, or portion thereof is in violation of any ordinance or regulation or any of the provisions of this code.

SECTION C109—MEANS OF APPEALS

**C109.1 General.** In order to hear and decide appeals of orders, decisions or determinations made by the *code official* relative to the application and interpretation of this code, there shall be and is hereby created a board of appeals. The board of appeals shall be appointed by the governing authority and shall hold office at its pleasure. The board shall adopt rules of procedure for conducting its business, and shall render all decisions and findings in writing to the appellant with a duplicate copy to the *code official*.

**C109.2 Limitations on authority.** An application for appeal shall be based on a claim that the true intent of this code or the rules legally adopted thereunder have been incorrectly interpreted, the provisions of this code do not fully apply or an equally good or better form of construction is proposed. The board shall not have authority to waive requirements of this code.

**C109.3 Qualifications.** The board of appeals shall consist of members who are qualified by experience and training on matters pertaining to the provisions of this code and are not employees of the jurisdiction.

**C109.4 Administration.** The *code official* shall take action in accordance with the decisions of the board.

SECTION C110—STOP WORK ORDER

**C110.1 Authority.** Where the *code official* finds any work regulated by this code being performed in a manner contrary to the provi- sions of this code or in a dangerous or unsafe manner, the *code official* is authorized to issue a stop work order.

**C110.2 Issuance.** The stop work order shall be in writing and shall be given to the *owner* of the property, the owner’s authorized agent or the person performing the work. Upon issuance of a stop work order, the cited work shall immediately cease. The stop work order shall state the reason for the order and the conditions under which the cited work is authorized to resume.

**C110.3 Emergencies.** Where an emergency exists, the *code official* shall not be required to give a written notice prior to stopping the work.

**C110.4 Failure to comply.** Any person who shall continue any work after having been served with a stop work order, except such work as that person is directed to perform to remove a violation or unsafe condition, shall be subject to fines established by the AHJ.

### DEFINITIONS



CHAPTER

**2** [CE]

**User notes:**

***About this chapter:*** *Codes, by their very nature, are technical documents. Every word, term and punctuation mark can add to or change the meaning of a technical requirement. It is necessary to maintain a consensus on the specific meaning of each term contained in the code. Chapter 2 performs this function by stating clearly what specific terms mean for the purposes of the code.*

SECTION C201—GENERAL

**C201.1 Scope.** Unless stated otherwise, the following words and terms in this code shall have the meanings indicated in this chapter.

**C201.2 Interchangeability.** Words used in the present tense include the future; words in the masculine gender include the feminine and neuter; the singular number includes the plural and the plural includes the singular.

**C201.3 Terms defined in other codes.** Terms thsat are not defined in this code but are defined in the *International Building Code*, *International Fire Code*, *International Fuel Gas Code*, *International Mechanical Code*, *International Plumbing Code* or the *International Residential Code* shall have the meanings ascribed to them in those codes.

**C201.4 Terms not defined.** Terms not defined by this chapter shall have ordinarily accepted meanings such as the context implies.

SECTION C202—GENERAL DEFINITIONS

**ABOVE-GRADE WALL.** See “*Wall, above-grade*.”

**ACCESS (TO).** That which enables a device, appliance or equipment to be reached by *ready access* or by a means that first requires the removal or movement of a panel or similar obstruction.

**ADDITION.** An extension or increase in the *conditioned space* floor area, number of stories or height of a *building*

or structure.

**AIR BARRIER.** One or more materials joined together in a continuous manner to restrict or prevent the passage of air through the *building thermal envelope* and its assemblies.

**AIR CURTAIN UNIT.** A device installed at the building entrance that generates and discharges a laminar airstream intended to prevent the *infiltration* of external, unconditioned air into the conditioned spaces or the loss of inte- rior, conditioned air to the outside.

**AIR LEAKAGE.** The uncontrolled airflow through the *building thermal envelope* caused by pressure differences across the *building thermal envelope*. Air leakage can be inward (*infiltration*) or outward (exfiltration) through the *building thermal envelope*.

**ALTERATION.** Any construction, retrofit or renovation to an existing structure other than *repair* or *addition*. Also, a change in a build- ing, electrical, gas, mechanical or plumbing system that involves an extension, *addition* or change to the arrangement, type or purpose of the original installation.

**APPROVED.** Acceptable to the *code official*.

**APPROVED AGENCY.** An established and recognized agency that is regularly engaged in conducting tests or furnishing inspection services, or furnishing product certification, where such agency has been *approved* by the *code official*.

**APPROVED SOURCE.** An independent person, firm or corporation *approved* by the code official, who is competent and experienced in the application of engineering principles to materials, methods or systems analyses.

**AUTOMATIC.** Self-acting, operating by its own mechanism when actuated by some impersonal influence, as, for example, a change in current strength, pressure, temperature or mechanical configuration (see “*Manual*”).

**BELOW-GRADE WALL.** See “*Wall, below-grade*.”

**BEST EFFICIENCY POINT (BEP).** The pump hydraulic power operating point (consisting of both flow and head conditions) that results in the maximum efficiency.

**BIOGAS.** A mixture of hydrocarbons that is a gas at 60°F (15.5°C) and 1 atmosphere of pressure that is produced through the anaerobic digestion of organic matter.

**BIOMASS WASTE.** Organic nonfossil material of biological origin that is a byproduct or a discarded product. *Biomass waste* includes municipal solid waste from biogenic sources; landfill gas; sludge waste; agricultural crop byproducts; straw; and other biomass solids, liquids and biogases, but excludes wood and wood-derived fuels (including black liquor), biofuel feedstock, biodiesel and fuel ethanol.

**BOILER, MODULATING.** A boiler that is capable of more than a single firing rate in response to a varying temperature or heating load.

**BOILER SYSTEM.** One or more boilers, their piping and controls that work together to supply steam or hot water to heat output devices remote from the boiler.

**BUBBLE POINT.** The refrigerant liquid saturation temperature at a specified pressure.

**BUILDING.** Any structure used or intended for supporting or sheltering any use or occupancy, including any mechanical systems, service water-heating systems and electric power and lighting systems located on the *building site* and supporting the *building*.

**BUILDING COMMISSIONING.** A process that verifies and documents that the selected building systems have been designed, installed and function according to the *owner*’s project requirements and *construction documents*, and to minimum code requirements.

**BUILDING ENTRANCE.** Any door, set of doors, doorway or other form of portal that is used to gain access to the *building* from the outside by the public.

**BUILDING SITE.** A contiguous area of land that is under the ownership or control of one entity.

**BUILDING THERMAL ENVELOPE.** The basement walls, *exterior walls*, floors, ceilings, roofs and any other building element assemblies that enclose *conditioned space* or provide a boundary between *conditioned space* and exempt or unconditioned space.

**CAPTIVE KEY OVERRIDE.** A lighting control that will not release the key that activates the override when the lighting is on.

**CAVITY INSULATION.** Insulating material located between framing members.

***C*-FACTOR (THERMAL CONDUCTANCE).** The coefficient of heat transmission (surface to surface) through a building component or assembly, equal to the time rate of heat flow per unit area and the unit temperature difference between the warm side and cold side surfaces (Btu/h × ft2 × °F) [W/(m2 × K)].

**CHANGE OF OCCUPANCY.** A change in the use of a *building* or a portion of a *building* that results in any of the following:

1. A *change of occupancy* classification.
2. A change from one group to another group within an occupancy classification.
3. Any change in use within a group for which there is a change in the application of the requirements of this code.

**CHI-FACTOR (****-FACTOR).** The heat loss factor for a single *thermal bridge* characterized as a point element of a *building thermal enve- lope* (Btu/h × °F) [W/k].

**CIRCULATING HOT WATER SYSTEM.** A specifically designed water distribution system where one or more pumps are operated in the service hot water piping to circulate heated water from the water-heating equipment to the fixture supply and back to the water-heat- ing equipment.

**CLEAN WATER PUMP.** A device that is designed for use in pumping water with a maximum nonabsorbent free solid content of 0.016 lb/ft3 (0.256 kg/m3) and with a maximum dissolved solid content of 3.1 lb/ft3 (49.66 kg/m3), provided that the total gas content of the water does not exceed the saturation volume, and disregarding any additives necessary to prevent the water from freezing at a mini- mum of 14°F (-10°C).

**CLIMATE ZONE.** A geographical region based on climatic criteria as specified in this code.

**CODE OFFICIAL.** The officer or other designated authority charged with the administration and enforcement of this code, or a duly authorized representative.

**COEFFICIENT OF PERFORMANCE (COP) − COOLING.** The ratio of the rate of heat removal to the rate of energy input, in consistent units, for a complete refrigerating system or some specific portion of that system under designated operating conditions.

**COEFFICIENT OF PERFORMANCE (COP) − HEATING.** The ratio of the rate of heat delivered to the rate of energy input, in consistent units, for a complete heat pump system, including the compressor and, if applicable, auxiliary heat, under designated operating conditions.

**COMMERCIAL BUILDING.** For this code, all buildings that are not included in the definition of “*Residential building*.”

**COMMERCIAL COOKING APPLIANCE.** Appliances used in a commercial food service establishment for heating or cooking food. For the purpose of this definition, a commercial food service establishment is where food is regularly prepared for sale or is prepared on a scale that is, by volume and frequency, not representative of domestic household cooking.

**COMMON AREAS.** All conditioned spaces within *Group R* occupancy buildings that are not *dwelling units* or *sleeping units*.

**COMMUNITY RENEWABLE ENERGY FACILITY.** A facility that produces energy harvested from *renewable energy resources* and is qualified as a community energy facility under applicable jurisdictional statutes and rules.

**COMPUTER ROOM.** A room whose primary function is to house equipment for the processing and storage of electronic data which has a design total *information technology equipment* (ITE) equipment power density less than or equal to 20 watts per square foot (20 watts per 0.092 m2) of conditioned area or a design total ITE equipment load less than or equal to 10 kW.

**CONDENSING UNIT.** A factory-made assembly of refrigeration components designed to compress and liquefy a specific refrigerant. The unit consists of one or more refrigerant compressors, refrigerant condensers (air-cooled, evaporatively cooled or water-cooled), condenser fans and motors (where used) and factory-supplied accessories.

**CONDITIONED FLOOR AREA.** The horizontal projection of the floors associated with the *conditioned space*.

**CONDITIONED SPACE.** An area, room or space that is enclosed within the *building thermal envelope* and is directly or indirectly heated or cooled. Spaces are indirectly heated or cooled where they communicate through openings with *conditioned spaces*, where they are separated from *conditioned spaces* by uninsulated walls, floors or ceilings, or where they contain uninsulated *ducts*, piping or other sources of heating or cooling.

**CONGREGATE LIVING FACILITIES.** A *building* or part thereof that contains *sleeping units* where residents share bathroom or kitchen facilities, or both.

**CONSTRUCTION DOCUMENTS.** Written, graphic and pictorial documents prepared or assembled for describing the design, location and physical characteristics of the elements of a project necessary for obtaining a building permit.

**CONTINUOUS INSULATION (ci).** Insulating material that is continuous across all structural members without *thermal bridges* other than fasteners and service openings. It is installed on the interior or exterior or is integral to any opaque surface of the *building thermal envelope*.

**CRAWL SPACE WALL.** The opaque portion of a wall that encloses a crawl space and is partially or totally below grade.

**CURTAIN WALL.** Fenestration products used to create an external nonload-bearing wall that is designed to separate the exterior and interior environments.

**DATA CENTER.** A room or series of rooms that share *data center systems*, whose primary function is to house equipment for the processing and storage of electronic data and that has a design total ITE equipment power density exceeding 20 watts per square foot (20 watts per 0.092 m2) of conditioned area and a total design ITE equipment load greater than 10 kW.

**DATA CENTER SYSTEMS.** HVAC systems and equipment, or portions thereof, used to provide cooling or *ventilation* in a *data center*.

**DAYLIGHT RESPONSIVE CONTROL.** A device or system that provides *automatic* control of electric light levels based on the amount of daylight in a space.

**DAYLIGHT ZONE.** That portion of a building’s interior floor area that is illuminated by natural light.

**DEDICATED OUTDOOR AIR SYSTEM (DOAS).** A ventilation system that supplies 100 percent outdoor air primarily for the purpose of

*ventilation* and that is a separate system from the *zone* space-conditioning system.

**DEHUMIDIFIER.** A self-contained, electrically operated and mechanically encased product with the sole purpose of dehumidifying the space consisting of the following:

1. A refrigerated surface (evaporator) that condenses moisture from the atmosphere.
2. A refrigerating system, including an electric motor.
3. An air-circulating fan.
4. A means for collecting or disposing of the condensate.

A dehumidifier does not include a portable air conditioner, room air conditioner or packaged terminal air conditioner.

**DEMAND CONTROL KITCHEN VENTILATION (DCKV).** A system that provides *automatic*, continuous control over exhaust hood and makeup air fan speed in response to temperature, optical or infrared (IR) sensors that monitor cooking activity or through direct communication with cooking appliances.

**DEMAND CONTROL VENTILATION (DCV).** A ventilation system capability that provides for the *automatic* reduction of outdoor air intake below design rates when the actual occupancy of spaces served by the system is less than design occupancy.

**DEMAND RECIRCULATION WATER SYSTEM.** A water distribution system where one or more pumps prime the service hot water piping with heated water upon a demand for hot water.

**DEMAND RESPONSE SIGNAL.** A signal that indicates a price or a request to modify electricity consumption for a limited time period.

**DEMAND RESPONSIVE CONTROL.** A control capable of receiving and automatically responding to a *demand response signal*.

**DESSICANT DEHUMIDIFICATION SYSTEM.** A mechanical dehumidification technology that uses a solid or liquid material to remove moisture from the air.

**DIRECT DIGITAL CONTROL (DDC).** A type of control where controlled and monitored analog or binary data, such as temperature and contact closures, are converted to digital format for manipulation and calculations by a digital computer or microprocessor, then converted back to analog or binary form to control physical devices.

**DUCT.** A tube or conduit utilized for conveying air. The air passages of self-contained systems are not to be construed as air *ducts*.

**DUCT SYSTEM.** A continuous passageway for the transmission of air that, in addition to *ducts*, includes duct fittings, dampers, plenums, fans and accessory air-handling equipment and appliances.

**DWELLING UNIT.** A single unit providing complete independent living facilities for one or more persons, including permanent provi- sions for living, sleeping, eating, cooking and sanitation.

**DX-DEDICATED OUTDOOR AIR SYSTEM UNIT (DX-DOAS UNIT).** A type of air-cooled, water-cooled or water source factory-assembled product that dehumidifies 100 percent outdoor air to a low dew point and includes reheat that is capable of controlling the supply dry-bulb temperature of the dehumidified air to the designated supply air temperature. It may precondition outdoor air with an *energy recovery ventilation system*.

**DYNAMIC GLAZING.** Any fenestration product that has the fully reversible ability to change its performance properties, including *U- factor*, *solar heat gain coefficient* (SHGC) or *visible transmittance* (VT).

**EAST-ORIENTED.** Facing within 45 degrees of true east to the south and within less than 22.5 degrees of true east to the north in the northern hemisphere or facing within 45 degrees of true east to the north and within less than 22.5 degrees of true east to the south in the southern hemisphere.

**ECONOMIZER, AIR.** A *duct* and damper arrangement and *automatic* control system that allows a cooling system to supply outside air to reduce or eliminate the need for mechanical cooling during mild or cold weather.

**ECONOMIZER, WATER.** A system where the supply air of a cooling system is cooled indirectly with water that is itself cooled by heat or mass transfer to the environment without the use of mechanical cooling.

**ENCLOSED SPACE.** A volume surrounded by solid surfaces such as walls, floors, roofs and openable devices, such as doors and operable windows.

**ENERGY ANALYSIS.** A method for estimating the annual energy use of the *proposed design* and *standard reference design* based on estimates of energy use.

**ENERGY COST.** The total estimated annual cost for *purchased energy* for the building functions regulated by this code, including applicable demand charges.

**ENERGY RECOVERY, SERIES.** A three-step process in which the first step is to remove energy from a single airstream without the use of mechanical cooling. In the second step, the airstream is mechanically cooled for the purpose of dehumidification. In the third step, the energy removed in the first step is reintroduced to the airstream.

**ENERGY RECOVERY RATIO, SERIES (SERR).** The difference between the dry-bulb air temperatures leaving the *series energy recovery* unit and leaving the dehumidifying coil divided by the difference between 75°F (24°C) and the dry-bulb temperature of the air leaving the dehumidifying cooling coil.

**ENERGY RECOVERY VENTILATION SYSTEM.** Systems that employ air-to-air heat exchangers to recover energy from exhaust air for the purpose of preheating, precooling, humidifying or dehumidifying outdoor *ventilation air* prior to supplying the air to a space, either directly or as part of an HVAC system.

**ENERGY SIMULATION TOOL.** An *approved* software program or calculation-based methodology that projects the annual energy use of a *building*.

**ENERGY STORAGE SYSTEM (ESS).** One or more devices, assembled together, capable of storing energy in order to supply electrical energy at a future time.

**ENERGY USE INTENSITY (EUI).** The metric indicating the total amount of energy consumed by a *building* in 1 year divided by the gross floor area of the *building*.

**ENTHALPY RECOVERY RATIO (ERR).** Change in the enthalpy of the outdoor air supply divided by the difference between the outdoor air and entering exhaust air enthalpy, expressed as a percentage.

**ENTRANCE DOOR.** A vertical *fenestration* product used for occupant ingress, egress and access in nonresidential buildings, including, but not limited to, exterior entrances utilizing latching hardware and *automatic* closers and containing over 50 percent glazing specif- ically designed to withstand heavy-duty usage.

**EQUIPMENT ROOM.** A space that contains either electrical equipment, mechanical equipment, machinery, water pumps or hydraulic pumps that are a function of the building’s services.

**EXTERIOR WALL.** Walls including both *above-grade walls* and basement walls.

**EXTERIOR WALL ENVELOPE.** A system or assembly of exterior wall components, including exterior wall finish materials, that provides protection of the building structural members, including framing and sheathing materials, and conditioned interior space from the detrimental effects of the exterior environment.

**FAN, EMBEDDED.** A fan that is part of a manufactured assembly where the assembly includes functions other than air movement.

**FAN ARRAY.** Multiple fans in parallel between two plenum sections in an air distribution system.

**FAN BRAKE HORSEPOWER (BHP).** The horsepower delivered to the fan’s shaft. Brake horsepower does not include the mechanical drive losses, such as that from belts and gears.

**FAN ELECTRICAL INPUT POWER.** The electrical input power in kilowatts required to operate an individual fan or *fan array* at design conditions. It includes the power consumption of motor controllers, where present.

**FAN ENERGY INDEX (FEI).** The ratio of the electric input power of a reference fan to the electric input power of the actual fan as calcu- lated in accordance with AMCA 208.

**FAN NAMEPLATE ELECTRICAL INPUT POWER.** The nominal electrical input power rating stamped on a fan assembly nameplate.

**FAN SYSTEM.** All the fans that contribute to the movement of air serving spaces that pass through a point of a common *duct*, plenum or cabinet.

**FAN SYSTEM, COMPLEX.** A *fan system* that combines a *single-cabinet fan system* with other supply fans, exhaust fans or both.

**FAN SYSTEM, EXHAUST OR RELIEF.** A *fan system* dedicated to the removal of air from interior spaces to the outdoors.

**FAN SYSTEM, RETURN.** A *fan system* dedicated to removing air from the interior where some or all the air is to be recirculated except during economizer operation.

**FAN SYSTEM, SINGLE-CABINET.** A fan system that supplies air to a space and recirculates the air, wherein a single cabinet houses a single fan, a single *fan array*, a single set of fans operating in parallel or fans or fan arrays in series.

**FAN SYSTEM, TRANSFER.** A *fan system* that exclusively moves air from one occupied space to another.

**FAN SYSTEM AIRFLOW.** The sum of the airflow of all fans with *fan electrical input power* greater than 1 kW at *fan system design condi- tions*, excluding the airflow that passes through downstream fans with *fan electrical input power* less than 1 kW.

**FAN SYSTEM BHP.** The sum of the *fan brake horsepower* of all fans that are required to operate at *fan system design conditions* to supply air from the heating or cooling source to the *conditioned spaces* and return it to the source or exhaust it to the outdoors.

**FAN SYSTEM DESIGN CONDITIONS.** Operating conditions that can be expected to occur during normal system operation that result in the highest supply fan airflow rate to *conditioned spaces* served by the system, other than during *air economizer* operation.

**FAN SYSTEM ELECTRICAL INPUT POWER.** The sum of the fan electrical power of all fans that are required to operate at *fan system design conditions* to supply air from the heating or cooling source to the *conditioned spaces* and/or return it to the source or exhaust it to the outdoors.

**FAN SYSTEM MOTOR NAMEPLATE HP.** The sum of the motor *nameplate horsepower* of all fans that are required to operate at design conditions to supply air from the heating or cooling source to the *conditioned spaces* and return it to the source or exhaust it to the outdoors.

**FAULT DETECTION AND DIAGNOSTICS (FDD) SYSTEM.** A software platform that utilizes building analytic algorithms to convert data provided by sensors and devices to automatically identify faults in building systems and provide a prioritized list of actionable reso- lutions to those faults based on cost or energy avoidance, comfort and maintenance impact.

**FENESTRATION.** Products classified as either skylights or vertical *fenestration*.

**FENESTRATION PRODUCT, FIELD-FABRICATED.** A fenestration product whose frame is made at the construction site of standard dimensional lumber or other materials that were not previously cut or otherwise formed with the specific intention of being used to fabricate a fenestration product or exterior door. Field-fabricated does not include site-built fenestration.

**FENESTRATION PRODUCT, SITE-BUILT.** A *fenestration* designed to be made up of field-glazed or field-assembled units using specific factory cut or otherwise factory-formed framing and glazing units. Examples of site-built fenestration include *storefront* systems, *curtain walls* and atrium roof systems.

***F*-FACTOR.** The perimeter heat loss factor per unit perimeter length of slab-on-grade floors (Btu/h × ft × °F) [W/(m × K)].

**FINANCIAL RENEWABLE ENERGY POWER PURCHASE AGREEMENT.** A financial arrangement between a renewable electricty gener- ator and a purchaser wherein the purchaser pays or guarantees a price to the generator for the project’s renewable generation. Also known as a “financial power purchase agreement” and “virtual power purchase agreement.”

**FLOOR AREA, NET.** The actual occupied area not including unoccupied accessory areas such as corridors, stairways, toilet rooms, mechanical rooms and closets.

**GENERAL LIGHTING.** Interior lighting that provides a substantially uniform level of illumination throughout a space.

**GREEN RETAIL TARIFF.** An electricity-rate structure qualified under applicable statutes or rules contracted by an electricity service provider to the building project owner to provide electricity generated with 100 percent *renewable energy resources* without the purchase of unbundled renewable energy certificates (RECs).

**GREENHOUSE.** A structure or a thermally isolated area of a *building* that maintains a specialized sunlit environment with a skylight roof ratio of 50 percent or more above the growing area exclusively used for, and essential to, the cultivation, protection or mainte- nance of plants. *Greenhouses* are those that are erected for a period of 180 days or more.

**GROUP R.** Buildings or portions of buildings that contain any of the following occupancies as established in the *International Building Code*:

1. Group R-1.
2. Group R-2 where located more than three stories in height above grade plane.
3. Group R-4 where located more than three stories in height above grade plane.

**HEAT TRAP.** An arrangement of piping and fittings, such as elbows, or a commercially available *heat trap* that prevents thermosy- phoning of hot water during standby periods.

**HEATED SLAB.** Slab-on-grade construction in which the heating elements, hydronic tubing or hot air distribution system is in contact with, or placed within or under, the slab.

**HIGH SPEED DOOR.** A nonswinging door used primarily to facilitate vehicular access or material transportation, with a minimum opening rate of 32 inches (813 mm) per second, a minimum closing rate of 24 inches (610 mm) per second and that includes an auto- matic-closing device.

**HIGH-CAPACITY GAS-FIRED WATER HEATER.** Gas-fired instantaneous *water heaters* with a rated input greater than 200,000 Btu/h (58.6 kW) and not less than 4,000 Btu/h per gallon (310 W per liter) of stored water. Also, gas-fired storage *water heaters* with a rated input both greater than 105,000 Btu/h (30.8 kW) and less than 4,000 Btu/h per gallon (310 W per liter) of stored water.

**HIGH-END TRIM.** A lighting control setting that limits the maximum power to individual luminaries or groups of luminaries in a space.

**HISTORIC BUILDING.** Any *building* or structure that is one or more of the following:

1. Listed, or certified as eligible for listing, by the State Historic Preservation Officer or the Keeper of the National Register of Historic Places, in the National Register of Historic Places.
2. Designated as historic under an applicable state or local law.
3. Certified as a contributing resource within a National Register-listed, state-designated or locally designated historic district.

**HORTICULTURAL LIGHTING.** Electric lighting used for horticultural production, cultivation or maintenance.

**HUMIDISTATIC CONTROLS.** *Automatic* controls used to maintain humidity at a setpoint.

**HVAC TOTAL SYSTEM PERFORMANCE RATIO (HVAC TSPR).** The ratio of the sum of a building’s annual heating and cooling load in thousands of Btu’s to the sum of annual site energy consumption of the building HVAC systems in Btu.

**IEC DESIGN H MOTOR.** An electric motor that meets all of the following:

1. It is an induction motor designed for use with three-phase power.
2. It contains a cage rotor.
3. It is capable of direct-on-line starting.
4. It has four, six or eight poles.
5. It is rated from 0.4 kW to 1600 kW at a frequency of 60 hertz.

**IEC DESIGN N MOTOR.** An electric motor that meets all of the following:

1. It is an induction motor designed for use with three-phase power.
2. It contains a cage rotor.
3. It is capable of direct-on-line starting.
4. It has two, four, six or eight poles.
5. It is rated from 0.4 kW to 1600 kW at a frequency of 60 hertz.

**INDOOR GROW.** A space, other than a *greenhouse*, used exclusively for and essential to horticultural production, cultivation or maintenance.

**INFILTRATION.** The uncontrolled inward *air leakage* into a *building* caused by the pressure effects of wind or the effect of differences in the indoor and outdoor air density or both.

**INFORMATION TECHNOLOGY EQUIPMENT (ITE).** Items including computers, data storage devices, servers and network and commu- nication equipment.

**INTEGRATED HVAC SYSTEM.** An HVAC system designed to handle both sensible and latent heat removal. *Integrated HVAC systems* include, but are not limited to, HVAC systems with a sensible heat ratio of 0.65 or less and the capability of providing cooling, dedi- cated outdoor air systems, single-package air conditioners with at least one refrigerant circuit providing hot gas reheat, and *dehumidifiers* modified to allow external heat rejection.

**INTEGRATED PART LOAD VALUE (IPLV).** A single-number figure of merit based on part-load EER, COP or kW/ton expressing part-load efficiency for air-conditioning and heat pump equipment on the basis of weighted operation at various load capacities for equipment.

**INTERNAL CURTAIN SYSTEM.** A system consisting of movable panels of fabric or plastic film used to cover and uncover the space enclosed in a *greenhouse* on a daily basis.

**ISOLATION DEVICES.** Devices that isolate HVAC *zones* so that they can be operated independently of one another. *Isolation devices*

include separate systems, isolation dampers and controls providing shutoff at terminal boxes.

**LABELED.** Equipment, materials or products to which have been affixed a label, seal, symbol or other identifying mark of a nationally recognized testing laboratory, *approved agency* or other organization concerned with product evaluation that maintains periodic inspection of the production of the *labeled* items and whose labeling indicates either that the equipment, material or product meets identified standards or has been tested and found suitable for a specified purpose.

**LARGE-DIAMETER CEILING FAN.** A ceiling fan that is greater than or equal to 841/2 inches (2.15 m) in diameter. These fans are some- times referred to as High-Volume, Low-Speed (HVLS) fans.

**LINER SYSTEM (Ls).** A system that includes the following:

1. A continuous vapor barrier liner membrane that is installed below the purlins and that is uninterrupted by framing members.
2. An uncompressed, unfaced insulation resting on top of the liner membrane and located between the purlins.

For multilayer installations, the last rated *R*-value of insulation is for unfaced insulation draped over purlins and then compressed when the metal roof panels are attached.

**LISTED.** Equipment, materials, products or services included in a list published by an organization acceptable to the *code official* and concerned with evaluation of products or services that maintains periodic inspection of production of *listed* equipment or materials or periodic evaluation of services and whose listing states either that the equipment, material, product or service meets identified standards or has been tested and found suitable for a specified purpose.

**LOW SLOPE.** A slope less than 2 units vertical in 12 units horizontal (17 percent slope) as applied to roofs.

**LOW-VOLTAGE DRY-TYPE DISTRIBUTION TRANSFORMER.** A transformer that is air-cooled, does not use oil as a coolant, has an input voltage less than or equal to 600 volts and is rated for operation at a frequency of 60 hertz.

**LUMINAIRE-LEVEL LIGHTING CONTROLS.** A lighting system consisting of one or more luminaires with embedded lighting control logic, occupancy and ambient light sensors, wireless networking capabilities and local override switching capability, where required.

**MANUAL.** Capable of being operated by personal intervention (see “*Automatic*”).

**NAMEPLATE HORSEPOWER.** The nominal motor output power rating stamped on the motor nameplate.

**NEMA DESIGN A MOTOR.** A squirrel-cage motor that meets all of the following:

1. It is designed to withstand full-voltage starting and develop locked-rotor torque as shown in paragraph 12.38.1 of NEMA MG 1.
2. It has pull-up torque not less than the values shown in paragraph 12.40.1 of NEMA MG 1.
3. It has breakdown torque not less than the values shown in paragraph 12.39.1 of NEMA MG 1.
4. It has a locked-rotor current higher than the values shown in paragraph 12.35.1 of NEMA MG 1 for 60 hertz and paragraph

12.35.2 of NEMA MG 1 for 50 hertz.

1. It has a slip at rated load of less than 5 percent for motors with fewer than 10 poles.

**NEMA DESIGN B MOTOR.** A squirrel-cage motor that meets all of the following:

1. It is designed to withstand full-voltage starting.
2. It develops locked-rotor, breakdown and pull-up torques adequate for general application as specified in Sections 12.38,

12.39 and 12.40 of NEMA MG1.

1. It draws locked-rotor current not to exceed the values shown in Section 12.35.1 for 60 hertz and Section 12.35.2 for 50 hertz of NEMA MG1.
2. It has a slip at rated load of less than 5 percent for motors with fewer than 10 poles.

**NEMA DESIGN C MOTOR.** A squirrel-cage motor that meets all of the following:

1. Designed to withstand full-voltage starting and develop locked-rotor torque for high-torque applications up to the values shown in paragraph 12.38.2 of NEMA MG1 (incorporated by reference, see A§431.15).
2. It has pull-up torque not less than the values shown in paragraph 12.40.2 of NEMA MG1.
3. It has breakdown torque not less than the values shown in paragraph 12.39.2 of NEMA MG1.
4. It has a locked-rotor current not to exceed the values shown in paragraph 12.35.1 of NEMA MG1 for 60 hertz and paragraph

12.35.2 for 50 hertz.

1. It has a slip at rated load of less than 5 percent.

**NETWORKED GUESTROOM CONTROL SYSTEM.** A control system, with access from the front desk or other central location associated with a *Group R*-1 *building*, that is capable of identifying the rented and unrented status of each guestroom according to a timed sched- ule, and is capable of controlling HVAC in each hotel and motel guestroom separately.

**NONSTANDARD PART LOAD VALUE (NPLV).** A single-number part-load efficiency figure of merit calculated and referenced to condi- tions other than IPLV conditions, for units that are not designed to operate at AHRI standard rating conditions.

**NORTH-ORIENTED.** Facing within 67.5 degrees of true north in the northern hemisphere or facing within 67.5 degrees of true south in the southern hemisphere.

**OCCUPANT SENSOR CONTROL.** An *automatic* control device or system that detects the presence or absence of people within an area and causes lighting, equipment or appliances to be regulated accordingly.

**OCCUPIED-STANDBY MODE.** Mode of operation when an HVAC *zone* is scheduled to be occupied and an occupant sensor indicates no occupants are within the zone.

**ON-SITE RENEWABLE ENERGY.** Energy from *renewable energy resources* harvested at the building project site.

**OPAQUE DOOR.** A door that is not less than 50 percent opaque in surface area.

**OWNER.** Any person, agent, operator, entity, firm or corporation having any legal or equitable interest in the property; or recorded in the official records of the state, county or municipality as holding an interest or title to the property; or otherwise having possession or control of the property, including the guardian of the estate of any such person, and the executor or administrator of the estate of such person if ordered to take possession of real property by a court.

**PARKING AREA, EXTERIOR.** Parking spaces, drive aisles and ramps that are not located within a *building*, or that are located on a roof.

**PARKING AREA, INTERIOR.** Parking spaces, drive aisles and ramps located within a *building*.

**PARKING GARAGE SECTION.** A part of an enclosed parking garage that is separated from all other parts of the garage by full-height solid walls or operable openings that are intended to remain closed during normal operation and where vehicles cannot pass to other parts of the garage. A parking garage can have one or more *parking garage sections*, and *parking garage sections* can include multiple floors.

**PHOTOSYNTHETIC PHOTON EFFICACY (PPE).** Photosynthetic photon flux emitted by a light source divided by its electrical input power in units of micromoles per second per watt, or micromoles per joule (μmol/J) between 400–700nm as defined by ANSI/ASABE S640.

**PHYSICAL RENEWABLE ENERGY POWER PURCHASE AGREEMENT.** A contract for the purchase of renewable electricity from a specific renewable electricity generator to a purchaser of renewable electricity.

**POWERED ROOF/WALL VENTILATORS.** A fan consisting of a centrifugal or axial impeller with an integral driver in a weather-resistant housing and with a base designed to fit, usually by means of a curb, over a wall or roof opening.

**PROCESS APPLICATION.** A manufacturing, industrial or commercial procedure or activity where the primary purpose is other than conditioning spaces and maintaining comfort and amenities for the occupants of a building.

**PROPOSED DESIGN.** A description of the proposed building used to estimate annual energy use for determining compliance based on simulated *building* performance and HVAC total system performance ratio.

**PSI-FACTOR (****-FACTOR).** The heat loss factor per unit length of a *thermal bridge* characterized as a linear element of a *building ther- mal envelope* (Btu/h × ft × °F) [W/(m × K)].

**PUMP ENERGY INDEX (PEI).** The ratio of a pump’s energy rating divided by the energy rating of a minimally compliant pump. For pumps with the constant load operating mode, the relevant PEI is PEICL. For pumps with the variable load operating mode, the rele- vant PEI is PEIVL.

**PURCHASED ENERGY.** Energy or power purchased for consumption and delivered to the building site.

**RADIANT HEATING SYSTEM.** A heating system that transfers heat to objects and surfaces within a *conditioned space*, primarily by infrared radiation.

**READY ACCESS (TO).** That which enables a device, appliance or equipment to be directly reached without requiring the removal or movement of any panel or similar obstruction.

**REFRIGERANT DEW POINT.** The refrigerant vapor saturation temperature at a specified pressure.

**REFRIGERATED WAREHOUSE COOLER.** An enclosed storage space capable of being refrigerated to temperatures above 32°F (0°C) that can be walked into and has a total chilled storage area of not less than 3,000 square feet (279 m2).

**REFRIGERATED WAREHOUSE FREEZER.** An enclosed storage space capable of being refrigerated to temperatures at or below 32°F (0°C) that can be walked into and has a total chilled storage area of not less than 3,000 square feet (279 m2).

**REFRIGERATION SYSTEM, LOW TEMPERATURE.** Systems for maintaining food product in a frozen state in refrigeration applications.

**REFRIGERATION SYSTEM, MEDIUM TEMPERATURE.** Systems for maintaining food product above freezing in refrigeration applications.

**REGISTERED DESIGN PROFESSIONAL.** An individual who is registered or licensed to practice their respective design profession as defined by the statutory requirements of the professional registration laws of the state or jurisdiction in which the project is to be constructed.

**RENEWABLE ENERGY CERTIFICATE (REC).** A market-based instrument that represents and conveys the environmental, social and other nonpower attributes of 1 megawatt hour of renewable electricity generation and could be sold separately from the underlying physical electricity associated with *renewable energy resources*, also known as energy attribute and energy attribute certificate (EAC).

**RENEWABLE ENERGY INVESTMENT FUND (REIF).** A fund established by a jurisdiction to accept payment from building project owners to construct or acquire interests in qualifying renewable energy systems, together with their associated RECs, on the building project owners’ behalf.

**RENEWABLE ENERGY RESOURCES.** Energy derived from solar radiation, wind, waves, tides, *biomass waste* or extracted from hot fluid or steam heated within the earth.

**REPAIR.** The reconstruction or renewal of any part of an existing building for the purpose of its maintenance or to correct damage.

**REPLACEMENT COST.** The cost to construct or replace an entire building with equal quality, construction type and square footage at current construction market labor and material rates.

**REROOFING.** The process of recovering or replacing an existing roof covering. See “*Roof recover*” and “*Roof replacement*.”

**RESIDENTIAL BUILDING.** For this code, includes detached one- and two-family dwellings and multiple single-family dwellings (town- houses) and *Group R*-2, R-3 and R-4 buildings three stories or less in height above grade plane.

**ROOF ASSEMBLY.** A system designed to provide weather protection and resistance to design loads. The system consists of a roof covering and roof deck or a single component serving as both the roof covering and the roof deck. A *roof assembly* includes the roof covering, underlayment, roof deck, insulation, vapor retarder and interior finish.

**ROOF RECOVER.** The process of installing an additional roof covering over an existing roof covering without removing the existing roof covering.

**ROOF REPAIR.** Reconstruction or renewal of any part of an existing roof for the purpose of its maintenance.

**ROOF REPLACEMENT.** An *alteration* that includes the removal of all existing layers of *roof assembly* materials down to the roof deck and the installation of replacement materials above the existing roof deck.

**ROOFTOP MONITOR.** A raised section of a roof containing vertical *fenestration* along one or more sides.

***R*-VALUE (THERMAL RESISTANCE).** The inverse of the time rate of heat flow through a body from one of its bounding surfaces to the other surface for a unit temperature difference between the two surfaces, under steady state conditions, per unit area (h × ft2 × °F/Btu) [(m2 × K)/W].

**SATURATED CONDENSING TEMPERATURE.** The saturation temperature corresponding to the measured refrigerant pressure at the condenser inlet for single component and azeotropic refrigerants, and the arithmetic average of the dew point and *bubble point* temperatures corresponding to the refrigerant pressure at the condenser entrance for zeotropic refrigerants.

**SENSIBLE ENERGY RECOVERY RATIO.** Change in the dry-bulb temperature of the outdoor air supply divided by the difference between the outdoor air and entering exhaust air dry-bulb temperatures, expressed as a percentage.

**SERVICE WATER HEATING.** Supply of hot water for purposes other than comfort heating.

**SIMULATED BUILDING PERFORMANCE.** A process in which the proposed building design is compared to a *standard reference design*

for the purposes of estimating relative energy use against a baseline to determine code compliance.

**SLEEPING UNIT.** A room or space in which people sleep that can include permanent provisions for living, eating, and either sanitation or kitchen facilities but not both. Such rooms and spaces that are part of a *dwelling unit* are not *sleeping units*.

**SMALL ELECTRIC MOTOR.** A general purpose alternating-current single-speed induction motor.

**SOLAR HEAT GAIN COEFFICIENT (SHGC).** The ratio of the solar heat gain entering the space through the *fenestration* assembly to the incident solar radiation. Solar heat gain includes directly transmitted solar heat and absorbed solar radiation that is then reradiated, conducted or convected into the space.

**SOUTH-ORIENTED.** Facing within 45 degrees of true south in the northern hemisphere or facing within 45 degrees of true north in the southern hemisphere.

**STANDARD REFERENCE DESIGN.** A version of the *proposed design* that meets the minimum requirements of this code and is used to determine the maximum annual energy use requirement for compliance based on total simulated building performance and HVAC total system performance ratio.

**STOREFRONT.** A system of doors and windows mulled as a composite fenestration structure that has been designed to resist heavy use. *Storefront* systems include, but are not limited to, exterior fenestration systems that span from the floor level or above to the ceil- ing of the same story on *commercial buildings*, with or without mulled windows and doors.

**SUBSTANTIAL IMPROVEMENT.** Any *repair*, reconstruction, rehabilitation, *alteration*, *addition* or other improvement of a *building* or structure, the cost of which equals or is more than 50 percent of the market value replacement cost of the structure before the improvement or repair is started. Where the structure has sustained substantial damage, as defined in the *International Building Code*, any *repairs* are considered *substantial improvement* regardless of the actual *repair* work performed. *Substantial improvement* does not include the following:

1. Improvement of a *building* ordered by the code official to correct health, sanitary or safety code violations and that are the minimum necessary to assure safe living conditions.
2. *Alteration* of a historic building where the *alteration* will not affect the designation as a historic building.

**TESTING UNIT ENCLOSURE AREA.** The area sum of all the boundary surfaces that define the *dwelling unit*, *sleeping unit* or *conditioned enclosed space,* including top/ceiling, bottom/floor and all side walls. This does not include interior partition walls within the *dwelling unit*, *sleeping unit* or *conditioned enclosed space*. Wall height shall be measured from the finished floor of the *conditioned space* to the finished floor or roof/ceiling *air barrier* above.

**THERMAL BLOCK.** A generic concept used in energy simulation. It can include one or more thermal zones. It represents a whole *build- ing* or portion of a *building* with the same use type served by the same HVAC system type.

**THERMAL BRIDGE.** An element or interface of elements that has higher thermal conductivity than the surrounding *building thermal envelope*, which creates a path of least resistance for heat transfer.

**THERMAL DISTRIBUTION EFFICIENCY (TDE).** The resistance to changes in air heat as air is conveyed through a distance of air *duct*. TDE is a heat loss calculation evaluating the difference in the heat of the air between the air duct inlet and outlet caused by differences in temperatures between the air in the *duct* and the duct material. TDE is expressed as a percent difference between the inlet and outlet heat in the *duct*.

**THERMOSTAT.** An *automatic* control device used to maintain temperature at a fixed or adjustable setpoint.

**TIME-SWITCH CONTROL.** An *automatic* control device or system that controls lighting or other loads, including switching off, based on time schedules.

***U*-FACTOR (THERMAL TRANSMITTANCE).** The coefficient of heat transmission (air to air) through a building component or assembly, equal to the time rate of heat flow per unit area and unit temperature difference between the warm side and cold side air films (Btu/h

× ft2 × °F) [W/(m2 × K)].

**VARIABLE REFRIGERANT FLOW SYSTEM.** An engineered direct-expansion (DX) refrigerant system that incorporates a common *condensing unit*, at least one variable-capacity compressor, a distributed refrigerant piping network to multiple indoor fan heating and cooling units each capable of individual zone temperature control, through integral zone temperature control devices and a common communications network. Variable refrigerant flow utilizes three or more steps of control on common interconnecting piping.

**VEGETATIVE ROOF.** An assembly of interacting components designed to waterproof a building’s top surface that includes, by design, vegetation and related landscape elements.

**VENTILATION.** The natural or mechanical process of supplying conditioned or unconditioned air to, or removing such air from, any space.

**VENTILATION AIR.** That portion of supply air that comes from outside (outdoors) plus any recirculated air that has been treated to maintain the desired quality of air within a designated space.

**VISIBLE TRANSMITTANCE (VT).** The ratio of visible light entering the space through the fenestration product assembly to the incident visible light. Visible transmittance includes the effects of glazing material and frame and is expressed as a number between 0 and 1.

**VISIBLE TRANSMITTANCE, ANNUAL (VTannual).** The ratio of visible light entering the space through the fenestration product assembly to the incident visible light during the course of a year, which includes the effects of glazing material, frame, and light well or tubular conduit, and is expressed as a number between 0 and 1.

**VOLTAGE DROP.** A decrease in voltage caused by losses in the wiring systems that connect the power source to the load.

**WALK-IN COOLER.** An enclosed storage space capable of being refrigerated to temperatures above 32°F (0°C) and less than 55°F (12.8°C) that can be walked into, has a ceiling height of not less than 7 feet (2134 mm) and has a total chilled storage area of less than 3,000 square feet (279 m2).

**WALK-IN FREEZER.** An enclosed storage space capable of being refrigerated to temperatures at or below 32°F (0°C) that can be walked into, has a ceiling height of not less than 7 feet (2134 mm) and has a total chilled storage area of less than 3,000 square feet (279 m2).

**WALL, ABOVE-GRADE.** A wall associated with the *building thermal envelope* that is more than 15 percent above grade and is on the exterior of the *building* or any wall that is associated with the *building thermal envelope* that is not on the exterior of the building. This includes, but is not limited to, between-floor spandrels, peripheral edges of floors, roof knee walls, dormer walls, gable end walls, walls enclosing a mansard roof, mechanical equipment penetrations and skylight shafts.

**WALL, BELOW-GRADE.** A wall associated with the basement or first story of the *building* that is part of the *building thermal envelope*, is not less than 85 percent below grade and is on the exterior of the building.

**WATER HEATER.** Any heating appliance or equipment that heats potable water and supplies such water to the potable hot water distribution system.

**WEST-ORIENTED.** Facing within 45 degrees of true west to the south and within less than 22.5 degrees of true west to the north in the northern hemisphere or facing within 45 degrees of true west to the north and within less than 22.5 degrees of true west to the south in the southern hemisphere.

**WORK AREA.** That portion or portions of a *building* consisting of all reconfigured spaces as indicated on the *construction documents*. *Work area* excludes other portions of the *building* where incidental work entailed by the intended work must be performed and portions of the building where work not initially intended by the *owner* is specifically required by this code.

**ZONE.** A space or group of spaces within a *building* with heating or cooling requirements that are sufficiently similar so that desired conditions can be maintained throughout using a single controlling device.

### GENERAL REQUIREMENTS



CHAPTER

**3** [CE]


**User notes:**

***About this chapter:*** *Chapter 3 addresses broadly applicable requirements that would not be at home in other chapters having more specific coverage of subject matter. This chapter establishes climate zone by US counties and territories and includes methodology for determining climate zones elsewhere. It also contains product rating, marking and installation requirements for materials such as insulation, windows, doors and siding.*

SECTION C301—CLIMATE ZONES

**C301.1 General.** *Climate zones* from Figure C301.1 or Table C301.1 shall be used for determining the applicable requirements from Chapter 4. Locations not indicated in Table C301.1 shall be assigned a *climate zone* in accordance with Section C301.3.

**FIGURE C301.1—CLIMATE ZONES**



|  |
| --- |
| **US STATES—continued** |
| **ILLINOIS** *(continued)* |
| 5A Henderson |
| 5A Henry |
| 5A Iroquois |
| 4A Jackson |
| 4A Jasper |
| 4A Jefferson |
| 4A Jersey |
| 5A Jo Daviess |
| 4A Johnson |
| 5A Kane |
| 5A Kankakee |
| 5A Kendall |
| 5A Knox |
| 5A Lake |
| 5A La Salle |
| 4A Lawrence |
| 5A Lee |
| 5A Livingston |
| 5A Logan |
| 5A Macon |
| 4A Macoupin |
| 4A Madison |
| 4A Marion |
| 5A Marshall |
| 5A Mason |
| 4A Massac |
| 5A McDonough |
| 5A McHenry |
| 5A McLean |
| 5A Menard |
| 5A Mercer |
| 4A Monroe |
| 4A Montgomery |
| 5A Morgan |
| 5A Moultrie |
| 5A Ogle |
| 5A Peoria |
| 4A Perry |
| 5A Piatt |
| 5A Pike |
| 4A Pope |
| 4A Pulaski |
| 5A Putnam |
| 4A Randolph |

|  |
| --- |
| 4A Richland |
| 5A Rock Island |
| 4A Saline |
| 5A Sangamon |
| 5A Schuyler |
| 5A Scott |
| 4A Shelby |
| 5A Stark |
| 4A St. Clair |
| 5A Stephenson |
| 5A Tazewell |
| 4A Union |
| 5A Vermilion |
| 4A Wabash |
| 5A Warren |
| 4A Washington |
| 4A Wayne |
| 4A White |
| 5A Whiteside |
| 5A Will |
| 4A Williamson |
| 5A Winnebago |
| 5A Woodford |
| **INDIANA** |
| 5A Adams |
| 5A Allen |
| 4A Bartholomew |
| 5A Benton |
| 5A Blackford |
| 5A Boone |
| 4A Brown |
| 5A Carroll |
| 5A Cass |
| 4A Clark |
| 4A Clay |
| 5A Clinton |
| 4A Crawford |
| 4A Daviess |
| 4A Dearborn |
| 4A Decatur |
| 5A De Kalb |
| 5A Delaware |
| 4A Dubois |
| 5A Elkhart |
| 4A Fayette |
| 4A Floyd |

**C301.2 Warm Humid counties.** In Table C301.1, Warm Humid counties are identified by an asterisk.

**C301.3 Climate zone definitions.** To determine the *climate zones* for locations not listed in this code, use the following information to determine *climate zone* numbers and letters in accordance with Items 1 through 5.

1. Determine the thermal climate zone, 0 through 8, from Table C301.3 using the heating (HDD) and cooling degree-days (CDD) for the location.
2. Determine the moisture zone (Marine, Dry or Humid) in accordance with Items 2.1 through 2.3.
   1. If monthly average temperature and precipitation data are available, use the Marine, Dry and Humid definitions to determine the moisture zone (C, B or A).
   2. If annual average temperature information (including degree-days) and annual precipitation (i.e., annual mean) are available, use Items 2.2.1 through 2.2.3 to determine the moisture zone. If the moisture zone is not Marine, then use the Dry definition to determine whether Dry or Humid.
      1. If thermal climate zone is 3 and CDD50°F ≤ 4,500 (CDD10°C ≤ 2500), climate zone is Marine (3C).
      2. If thermal climate zone is 4 and CDD50°F ≤ 2,700 (CDD10°C ≤ 1500), climate zone is Marine (4C).
      3. If thermal climate zone is 5 and CDD50°F ≤ 1,800 (CDD10°C ≤ 1000), climate zone is Marine (5C).
   3. If only degree-day information is available, use Items 2.3.1 through 2.3.3 to determine the moisture zone. If the moisture zone is not Marine, then it is not possible to assign Humid or Dry moisture zone for this location.
      1. If thermal climate zone is 3 and CDD50°F ≤ 4,500 (CDD10°C ≤ 2500), climate zone is Marine (3C).
      2. If thermal climate zone is 4 and CDD50°F ≤ 2,700 (CDD10°C ≤ 1500), climate zone is Marine (4C).
      3. If thermal climate zone is 5 and CDD50°F ≤ 1,800 (CDD10°C ≤ 1000), climate zone is Marine (5C).
3. Marine (C) Zone definition: Locations meeting all the criteria in Items 3.1 through 3.4.
   1. Mean temperature of coldest month between 27°F (-3°C) and 65°F (18°C).
   2. Warmest month mean < 72°F (22°C).
   3. Not fewer than four months with mean temperatures over 50°F (10°C).
   4. Dry season in summer. The month with the heaviest precipitation in the cold season has at least three times as much precipitation as the month with the least precipitation in the rest of the year. The cold season is October through March in the Northern Hemisphere and April through September in the Southern Hemisphere.
4. Dry (B) definition: Locations meeting the criteria in Items 4.1 through 4.4.
   1. Not Marine (C).
   2. If 70 percent or more of the precipitation, *P*, occurs during the high sun period, defined as April through September in the Northern Hemisphere and October through March in the Southern Hemisphere, then the dry/humid thresh- old is in accordance with Equation 3-1.

**Equation 3-1** *P* < 0.44 × (*T* – 7)

[*P* < 20.0 × (*T* + 14) in SI units]

where:

*P* = Annual precipitation, inches (mm).

*T* = Annual mean temperature, °F (°C).

* 1. If between 30 and 70 percent of the precipitation, *P*, occurs during the high sun period, defined as April through September in the Northern Hemisphere and October through March in the Southern Hemisphere, then the dry/humid threshold is in accordance with Equation 3-2.

**Equation 3-2** *P* < 0.44 × (*T* – 19.5)

[*P* < 20.0 × (*T* + 7) in SI units]

where:

*P* = Annual precipitation, inches (mm).

*T* = Annual mean temperature, °F (°C).

* 1. If 30 percent or less of the precipitation, *P*, occurs during the high sun period, defined as April through September in the Northern Hemisphere and October through March in the Southern Hemisphere, then the dry/humid thresh- old is in accordance with Equation 3-3.

**Equation 3-3** *P* < 0.44 × (*T* – 32)

[*P* < 20.0 × *T* in SI units]

where:

*P* = Annual precipitation, inches (mm).

*T* = Annual mean temperature, °F (°C).

1. Humid (A) definition: Locations that are not Marine (C) or Dry (B).

|  |  |  |
| --- | --- | --- |
| **TABLE C301.3—THERMAL CLIMATE ZONE DEFINITIONS** | | |
| **ZONE NUMBER** | **THERMAL CRITERIA** | |
| **IP Units** | **SI Units** |
| 0 | 10,800 < CDD50°F | 6000 < CDD10°C |
| 1 | 9,000 < CDD50°F < 10,800 | 5000 < CDD10°C < 6000 |
| 2 | 6,300 < CDD50°F ≤ 9,000 | 3500 < CDD10°C ≤ 5000 |
| 3 | CDD50°F ≤ 6,300 AND HDD65°F ≤ 3,600 | CDD10°C < 3500 AND HDD18°C ≤ 2000 |
| 4 | CDD50°F ≤ 6,300 AND 3,600 < HDD65°F ≤ 5,400 | CDD10°C < 3500 AND 2000 < HDD18°C ≤ 3000 |
| 5 | CDD50°F < 6,300 AND 5,400 < HDD65°F ≤ 7,200 | CDD10°C < 3500 AND 3000 < HDD18°C ≤ 4000 |
| 6 | 7,200 < HDD65°F ≤ 9,000 | 4000 < HDD18°C ≤ 5000 |
| 7 | 9,000 < HDD65°F ≤ 12,600 | 5000 < HDD18°C ≤ 7000 |
| 8 | 12,600 < HDD65°F | 7000 < HDD18°C |
| For SI: °C = [(°F) – 32]/1.8. | | |

**C301.4 Tropical climate region.** The tropical climate region shall be defined as:

1. Hawaii, Puerto Rico, Guam, American Samoa, US Virgin Islands, Commonwealth of Northern Mariana Islands; and
2. Islands in the area between the Tropic of Cancer and the Tropic of Capricorn.

SECTION C302—DESIGN CONDITIONS

**C302.1 Interior design conditions.** The interior design temperatures used for heating and cooling load calculations shall be a maxi- mum of 72°F (22°C) for heating and minimum of 75°F (24°C) for cooling.

SECTION C303—MATERIALS, SYSTEMS AND EQUIPMENT

**C303.1 Identification.** Materials, systems and equipment shall be identified in a manner that will allow a determination of compliance with the applicable provisions of this code.

**C303.1.1 Building thermal envelope insulation.** An *R-value* identification mark shall be applied by the manufacturer to each piece of *building thermal envelope* insulation 12 inches (305 mm) or greater in width. Alternatively, the insulation installers shall provide a certification listing the type, manufacturer and *R-value* of insulation installed in each element of the *building thermal envelope*. For blown-in or sprayed fiberglass and cellulose insulation, the initial installed thickness, settled thickness, settled *R-value*, installed density, coverage area and number of bags installed shall be indicated on the certification. For sprayed polyurethane foam (SPF) insulation, the installed thickness of the areas covered and *R-value* of installed thickness shall be indicated on the certification. For insulated siding, the *R-value* shall be *labeled* on the product’s package and shall be indicated on the certification. The insulation installer shall sign, date and post the certification in a conspicuous location on the job site.

**Exception:** For roof insulation installed above the deck, the *R-value* shall be *labeled* as required by the material standards specified in Table 1508.2 of the *International Building Code*.

**C303.1.1.1 Blown-in or sprayed roof/ceiling insulation.** The thickness of blown-in or sprayed fiberglass and cellulose roof/ceiling insulation shall be written in inches (mm) on markers and one or more of such markers shall be installed for every 300 square feet (28 m2) of attic area throughout the attic space. The markers shall be affixed to the trusses or joists and marked with the minimum initial installed thickness with numbers not less than 1 inch (25 mm) in height. Each marker shall face the attic *access* opening. Spray polyurethane foam thickness and installed *R-value* shall be indicated on certification provided by the insulation installer.

**C303.1.2 Insulation mark installation.** Insulating materials shall be installed such that the manufacturer’s *R-value* mark is read- ily observable upon inspection. For insulation materials that are installed without an observable manufacturer’s *R-value* mark, such as blown or draped products, an insulation certificate complying with Section C303.1.1 shall be left immediately after instal- lation by the installer, in a conspicuous location within the *building*, to certify the installed *R-value* of the insulation material.

**Exception:** For roof insulation installed above the deck, the *R-value* shall be *labeled* as specified by the material standards in Table 1508.2 of the *International Building Code*.

**C303.1.3 Fenestration product rating.** *U-factors*, *solar heat gain coefficient* (SHGC) and visible transmittance (VT) of fenestration products shall be determined as follows:

* 1. For windows, doors and skylights, *U-factor*, SHGC and VT ratings shall be determined in accordance with NFRC 100 and NFRC 200.
  2. Where required for garage doors and rolling doors, *U-factor* ratings shall be determined in accordance with either NFRC 100 or ANSI/DASMA 105.

*U-factors*, SHGC and VT shall be determined by an accredited, independent laboratory, and *labeled* and certified by the manu- facturer with a label affixed to the product or a label certificate specific to the products in the project.

Products lacking such a *labeled U-factor* shall be assigned a default *U-factor* from Table C303.1.3(1) or Table C303.1.3(2). Prod- ucts lacking such a *labeled* SHGC or VT shall be assigned a default SHGC or VT from Table C303.1.3(3). For Tubular Daylighting Devices, VTannual shall be measured and rated in accordance with NFRC 203.

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **TABLE C303.1.3(1)—DEFAULT GLAZED WINDOW, GLASS DOOR AND SKYLIGHT *U*-FACTORS** | | | | |
| **FRAME TYPE** | **WINDOW AND GLASS DOOR** | | **SKYLIGHT** | |
| **Single** | **Double** | **Single** | **Double** |
| Metal | 1.20 | 0.80 | 2.00 | 1.30 |
| Metal with thermal break | 1.10 | 0.65 | 1.90 | 1.10 |
| Nonmetal or metal clad | 0.95 | 0.55 | 1.75 | 1.05 |
| Glass block | 0.60 | | | |

|  |  |
| --- | --- |
| **TABLE C303.1.3(2)—DEFAULT OPAQUE DOOR *U*-FACTORS** | |
| **DOOR TYPE** | **OPAQUE *U*-FACTOR** |
| Uninsulated metal | 1.20 |
| Insulated metal (rolling) | 0.90 |
| Insulated metal (other) | 0.60 |
| Wood | 0.50 |
| Insulated, nonmetal edge, max 45% glazing, any glazing double pane | 0.35 |

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| **TABLE C303.1.3(3)—DEFAULT GLAZED FENESTRATION SHGC AND VT** | | | | | |
|  | **SINGLE GLAZED** | | **DOUBLE GLAZED** | | **GLAZED BLOCK** |
| **Clear** | **Tinted** | **Clear** | **Tinted** |
| SHGC | 0.8 | 0.7 | 0.7 | 0.6 | 0.6 |
| VT | 0.6 | 0.3 | 0.6 | 0.3 | 0.6 |

**C303.1.4 Insulation product rating.** The thermal resistance (*R-value*) of insulation shall be determined in accordance with the US Federal Trade Commission *R*-value rule (CFR Title 16, Part 460) in units of h × ft2 × °F/Btu at a mean temperature of 75°F (24°C).

**C303.1.4.1 Insulated siding.** The thermal resistance (*R-value*) of insulated siding shall be determined in accordance with ASTM C1363. Installation for testing shall be in accordance with the manufacturer’s instructions.

**C303.2 Installation.** Materials, systems and equipment shall be installed in accordance with the manufacturer’s instructions and the

*International Building Code*.

**C303.2.1 Protection of exposed foundation insulation.** Insulation applied to the exterior of basement walls, *crawl space walls* and the perimeter of slab-on-grade floors shall have a rigid, opaque and weather-resistant protective covering to prevent the degradation of the insulation’s thermal performance. The protective covering shall cover the exposed exterior insulation and extend not less than 6 inches (153 mm) below grade.

**C303.2.2 Multiple layers of continuous insulation board.** Where two or more layers of continuous insulation board are used in a construction assembly, the continuous insulation boards shall be installed in accordance with Section C303.2. Where the continuous insulation board manufacturer’s instructions do not address installation of two or more layers, the edge joints between each layer of continuous insulation boards shall be staggered.

### COMMERCIAL ENERGY EFFICIENCY



CHAPTER

**4** [CE]

**User notes:**

***About this chapter:*** *Chapter 4 presents the paths and options for compliance with the energy efficiency provisions. Chapter 4 contains energy efficiency provisions for the building envelope, mechanical and water-heating systems, lighting and additional efficiency requirements. A performance alternative is also provided to allow for energy code compliance other than by the prescriptive method.*

SECTION C401—GENERAL

**C401.1 Scope.** The provisions in this chapter are applicable to *commercial buildings* and their *building sites*.

**C401.2 Application.** *Commercial buildings* shall comply with Section C401.2.1 or C401.2.2.

**C401.2.1 International Energy Conservation Code.** *Commercial buildings* shall comply with one of the following:

1. Prescriptive Compliance. The Prescriptive Compliance option requires compliance with Sections C402 through C406, ~~and~~ Section C408 and appendices CG, CI, and CJ. A *Dwelling units* and *sleeping units* in Group R-2 buildings shall be deemed to be in compliance with this chapter, provided that they comply with Section R406.
2. *Simulated Building Performance*. The *Simulated Building Performance* option requires compliance with Section C407.

**Exception:** *Additions*, *alterations*, *repairs* and changes of occupancy to existing buildings complying with Chapter 5.

**C401.2.2 ASHRAE 90.1.** *Commercial buildings* shall comply with the requirements of ANSI/ASHRAE/IES 90.1 Appendix CK and the requirements of the sections indicated within Table C401.2.2.

**TABLE C401.2.2**

**REQUIREMENTS FOR ASHRAE 90.1 COMPLIANCE**

|  |  |
| --- | --- |
| SECTIONa | TITLE |
| New Construction | |
| C405.4 | Horticultural lighting |
| Appendix CG | Electric vehicle power transfer infrastructure |
| Appendix CJ | Electrical energy storage system |
| C405.17 | Electric infrastructure |
| Additions and Alterations | |
| C502.3.7 | Additional energy efficiency credit requirements |
| C503.3.2 | Mechanical system acceptance testing |
| C503.3.3 | Duct testing |
| C503.3.4 | Controls |
| C503.3.5 | System sizing |
| C503.6 | Additional energy efficiency credit requirements for alterations |
| C505.1.3 | Additional energy efficiency for changes of occupancy |

a. Reference to a code section includes all the relative subsections as indicated in the table.

**C401.3 Building thermal envelope certificate.** A permanent *building thermal envelope* certificate shall be completed by an *approved* party. Such certificate shall be posted on a wall in the space where the space conditioning equipment is located, a utility room or other *approved* location. If located on an electrical panel, the certificate shall not cover or obstruct the visibility of the circuit directory label, service disconnect label or other required labels. A copy of the certificate shall also be included in the construction files for the project. The certificate shall include the following:

1. *R*-values of insulation installed in or on ceilings, roofs, walls, foundations and slabs, *basement walls*, *crawl space walls* and floors and *ducts* outside *conditioned spaces*.
2. *U-factors* and *solar heat gain coefficients* (SHGC) of *fenestrations*.
3. Results from any *building thermal envelope air leakage* testing performed on the *building*.

Where there is more than one value for any component of the *building thermal envelope*, the certificate shall indicate the area- weighted average value where available. If the area-weighted average is not available, the certificate shall list each value that applies to 10 percent or more of the total component area.

SECTION C402—BUILDING THERMAL ENVELOPE REQUIREMENTS

**C402.1 General.** *Building thermal envelope* assemblies for buildings that are intended to comply with the code on a prescriptive basis in accordance with the compliance path described in Item 1 of Section C401.2.1 shall comply with the following:

* 1. The opaque portions of the *building thermal envelope* shall comply with the specific insulation require- ments of Section C402.2 and the thermal requirements of Section C402.1.2, C402.1.3 or C402.1.4. Where the total area of through penetrations of mechanical equipment is greater than 1 percent of the opaque *above-grade wall* area, the *building thermal envelope* shall comply with Section C402.1.2.1.8.
  2. Wall solar reflectance and thermal *emittance* shall comply with Section C402.3.
  3. Roof solar reflectance and thermal *emittance* shall comply with Section C402.4.
  4. *Fenestration* in the *building thermal envelope* shall comply with Section C402.5. Where *buildings* have a vertical *fenestration* area or skylight area greater than that allowed in Section C402.5, the *building* and *building thermal envelope* shall comply with Item 2 of Section C401.2.1, C401.2.2 or C402.1.4.
  5. *Air leakage* of *building thermal envelope* shall comply with Section C402.6.
  6. *Thermal bridges* in *above-grade walls* shall comply with Section C402.7.
  7. *Walk-in coolers*, *walk-in freezers*, *refrigerated warehouse coolers* and *refrigerated warehouse freezers* shall comply with Section C403.12.

**C402.1.1 Low-energy buildings and greenhouses.** The following low-energy buildings, or portions thereof separated from the remainder of the *building* by *building thermal envelope* assemblies complying with this section, shall be exempt from the *building thermal envelope* provisions of Section C402.

**C402.1.1.1 Low-energy buildings.** *Buildings* that comply with either of the following:

* + 1. Those with a peak design rate of energy usage less than 3.4 Btu/h × ft2 (10.7 W/m2 ) or 1.0 watt per square foot (10.7 W/m2) of floor area for space conditioning purposes.
    2. Those that do not contain *conditioned space*.

**C402.1.1.2 Greenhouses.** *Greenhouse* structures or areas that are mechanically heated or cooled and that comply with all of the following shall be exempt from the *building thermal envelope* requirements of this code:

1. Exterior opaque envelope assemblies comply with Sections C402.2 and C402.5.5.

**Exception:** Low energy greenhouses that comply with Section C402.1.1.

1. Interior partition *building thermal envelope* assemblies that separate the *greenhouse* from *conditioned space* comply with Sections C402.2, C402.5.3 and C402.5.5.
2. *Fenestration* assemblies that comply with the *building thermal envelope* requirements in Table C402.1.1.2. The *U-factor*

for a roof shall be for the *roof assembly* or a roof that includes the assembly and an *internal curtain system*.

**Exception:** Unconditioned greenhouses.

|  |  |
| --- | --- |
| **TABLE C402.1.1.2—FENESTRATION BUILDING THERMAL ENVELOPE MAXIMUM REQUIREMENTS** | |
| **COMPONENT** | ***U*-FACTOR (Btu/h × ft2 × °F)** |
| Skylight | 0.5 |
| Vertical fenestration | 0.7 |

**C402.1.1.3 Equipment buildings.** *Buildings* that comply with the following shall be exempt from the *building thermal enve- lope* provisions of this code:

1. Are separate *buildings* with floor area not more than 1,200 square feet (111 m2).
2. Are intended to house electric equipment with installed equipment power totaling not less than 7 watts per square foot (75 W/m2) and not intended for human occupancy.
3. Have a heating system capacity not greater than 20,000 Btu/h (6 kW) and a heating *thermostat* setpoint that is restricted to not more than 50°F (10°C).
4. Have an average wall and roof *U-factor* less than 0.2 in Climate Zones 1 through 5 and less than 0.12 in Climate Zones 6 through 8.
5. Comply with the roof solar reflectance and thermal *emittance* provisions for Climate Zone 1.

**C402.1.2 Assembly *U*-factor, *C*-factor or *F*-factor method.** *Building thermal envelope* opaque assemblies shall have a *U-*, *C*- or *F- factor* not greater than that specified in Table C402.1.2. *Commercial buildings* or portions of *commercial buildings* enclosing *Group R* occupancies shall use the *U-*, *C*- or *F-factor* from the “*Group R*” column of Table C402.1.2. *Commercial buildings* or portions of *commercial buildings* enclosing occupancies other than *Group R* shall use the *U-*, *C*- or *F*-factor from the “All other” column of Table C402.1.2

**COMMERCIAL ENERGY EFFICIENCY**

**70**

**2024 INTERNATIONAL ENERGY CONSERVATION CODE®**

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE C402.1.2—OPAQUE BUILDING THERMAL ENVELOPE ASSEMBLY MAXIMUM REQUIREMENTS, *U*-FACTOR METHODa, b** | | | | | | | | | | | | | | | | |
| **CLIMATE ZONE** | **0 AND 1** | | **2** | | **3** | | **4 EXCEPT MARINE** | | **5 AND MARINE 4** | | **6** | | **7** | | **8** | |
| **All Other** | **Group R** | **All Other** | **Group R** | **All Other** | **Group R** | **All Other** | **Group R** | **All Other** | **Group R** | **All Other** | **Group R** | **All Other** | **Group R** | **All Other** | **Group R** |
| **Roofs** | | | | | | | | | | | | | | | | |
| Insulation entirely above roof deck | U-0.048 | U-0.039 | U-0.039 | U-0.039 | U-0.039 | U-0.039 | U-0.032 | U-0.032 | U-0.032 | U-0.032 | U-0.032 | U-0.032 | U-0.028 | U-0.028 | U-0.028 | U-0.028 |
| Metal buildings | U-0.035 | U-0.035 | U-0.035 | U-0.035 | U-0.035 | U-0.035 | U-0.035 | U-0.035 | U-0.035 | U-0.035 | U-0.031 | U-0.029 | U-0.029 | U-0.029 | U-0.026 | U-0.026 |
| Attic and other | U-0.027 | U-0.027 | U-0.027 | U-0.027 | U-0.027 | U-0.027 | U-0.021 | U-0.021 | U-0.021 | U-0.021 | U-0.021 | U-0.021 | U-0.017 | U-0.017 | U-0.017 | U-0.017 |
| **Walls, above grade** | | | | | | | | | | | | | | | | |
| Massf | U-0.151 | U-0.151 | U-0.151 | U-0.123 | U-0.123 | U-0.104 | U-0.104 | U-0.090 | U-0.090 | U-0.080 | U-0.080 | U-0.071 | U-0.071 | U-0.071 | U-0.037 | U-0.037 |
| Metal building | U-0.079 | U-0.079 | U-0.079 | U-0.079 | U-0.079 | U-0.052 | U-0.052 | U-0.050 | U-0.050 | U-0.050 | U-0.050 | U-0.050 | U-0.044 | U-0.039 | U-0.039 | U-0.039 |
| Metal framed | U-0.077 | U-0.077 | U-0.077 | U-0.064 | U-0.064 | U-0.064 | U-0.064 | U-0.064 | U-0.055 | U-0.055 | U-0.049 | U-0.049 | U-0.049 | U-0.042 | U-0.037 | U-0.037 |
| Wood framed and otherc | U-0.064 | U-0.064 | U-0.064 | U-0.064 | U-0.064 | U-0.064 | U-0.064 | U-0.064 | U-0.051 | U-0.051 | U-0.051 | U-0.051 | U-0.051 | U-0.051 | U-0.032 | U-0.032 |
| **Walls, below grade** | | | | | | | | | | | | | | | | |
| Below-grade wallc | C-1.140e | C-1.140e | C-1.140e | C-1.140e | C-1.140e | C-1.140e | C-0.119 | C-0.092 | C-0.119 | C-0.092 | C-0.092 | C-0.063 | C-0.063 | C-0.063 | C-0.063 | C-0.063 |
| **Floors** | | | | | | | | | | | | | | | | |
| Massd | U-0.322e | U-0.322e | U-0.107 | U-0.087 | U-0.074 | U-0.074 | U-0.057 | U-0.051 | U-0.057 | U-0.051 | U-0.051 | U-0.051 | U-0.042 | U-0.042 | U-0.038 | U-0.038 |
| Joist/framing | U-0.066e | U-0.066e | U-0.033 | U-0.033 | U-0.033 | U-0.033 | U-0.033 | U-0.033 | U-0.033 | U-0.033 | U-0.027 | U-0.027 | U-0.027 | U-0.027 | U-0.027 | U-0.027 |
| **Slab-on-grade floors** | | | | | | | | | | | | | | | | |
| Unheated slabs | F-0.73e | F-0.73e | F-0.73e | F-0.73e | F-0.73e | F-0.54 | F-0.52 | F-0.52 | F-0.52 | F-0.51 | F-0.51 | F-0.434 | F-0.51 | F-0.434 | F-0.434 | F-0.424 |
| Heated slabs | F-0.69 | F-0.69 | F-0.69 | F-0.69 | F-0.66 | F-0.66 | F-0.62 | F-0.62 | F-0.62 | F-0.62 | F-0.62 | F-0.602 | F-0.602 | F-0.602 | F-0.602 | F-0.602 |
| **Opaque doors** | | | | | | | | | | | | | | | | |
| Nonswinging door | U-0.31 | U-0.31 | U-0.31 | U-0.31 | U-0.31 | U-0.31 | U-0.31 | U-0.31 | U-0.31 | U-0.31 | U-0.31 | U-0.31 | U-0.31 | U-0.31 | U-0.31 | U-0.31 |
| Swinging doorg | U-0.37 | U-0.37 | U-0.37 | U-0.37 | U-0.37 | U-0.37 | U-0.37 | U-0.37 | U-0.37 | U-0.37 | U-0.37 | U-0.37 | U-0.37 | U-0.37 | U-0.37 | U-0.37 |
| Garage door < 14% glazingh | U-0.31 | U-0.31 | U-0.31 | U-0.31 | U-0.31 | U-0.31 | U-0.31 | U-0.31 | U-0.31 | U-0.31 | U-0.31 | U-0.31 | U-0.31 | U-0.31 | U-0.31 | U-0.31 |
| For SI: 1 pound per square foot = 4.88 kg/m2, 1 pound per cubic foot = 16 kg/m3.   1. Where assembly *U*-factors, *C*-factors and *F*-factors are established in ANSI/ASHRAE/IES 90.1 Appendix A, such opaque assemblies shall be a compliance alternative where those values meet the criteria of this table, and provided that the construction, excluding the cladding system on walls, complies with the appropriate construction details from ANSI/ASHRAE/IES 90.1 Appendix A. 2. Where *U*-factors have been established by testing in accordance with ASTM C1363, such opaque assemblies shall be a compliance alternative where those values meet the criteria of this table. The *R*-value of continuous insulation shall be permitted to be added to or subtracted from the original tested design. 3. Where heated slabs are below grade, below-grade walls shall comply with the *U*-factor requirements for above-grade mass walls. 4. “Mass floors” shall be in accordance with Section C402.1.3.4. 5. These *C*-, *F*- and *U*-factors are based on assemblies that are not required to contain insulation. 6. “Mass walls” shall be in accordance with Section C402.1.3.4. 7. Swinging door *U*-factors shall be determined in accordance with NFRC-100. 8. Garage doors having a single row of fenestration shall have an assembly *U*-factor less than or equal to 0.44 in Climate Zones 0 through 6 and less than or equal to 0.36 in Climate Zones 7 and 8, provided that the fenestration area is not less than 14 percent and not more than 25 percent of the total door area. | | | | | | | | | | | | | | | | |

**C402.1.2.1 Methods of determining *U*-, *C*- and *F*-factors.** Where assembly *U-factors*, *C*-factors and *F*-factors and calculation procedures are established in ANSI/ASHRAE/IES 90.1 Appendix A for opaque assemblies, such opaque assemblies shall be a compliance alternative provided they meet the criteria of Table C402.1.2 and the construction, excluding cladding system on walls, complies with the applicable construction details from ANSI/ASHRAE/IES 90.1 Appendix A. Where *U-factors* have been established by testing in accordance with ASTM C1363, such opaque assemblies shall be a compliance alternative provided they meet the criteria of Table C402.1.4. The *R-value* of *continuous insulation* shall be permitted to be added to or subtracted from the original tested design. Airspaces used for assembly evaluations shall comply with Section C402.2.7.

**C402.1.2.1.1 Tapered, above-deck insulation based on thickness.** For tapered, above-deck roof insulation, area- weighted *U-factors* of non-uniform insulation thickness shall be determined by an *approved* method.

**Exception:** The area-weighted *U*-factor shall be permitted to be determined by using the inverse of the average *R*-value determined in accordance with the exception to Section C402.1.3.2.

**C402.1.2.1.2 Suspended ceilings.** Insulation installed on suspended ceilings having removable ceiling tiles shall not be considered part of the assembly *U-factor* of the roof-ceiling construction.

**C402.1.2.1.3 Concrete masonry units, integral insulation.** In determining compliance with Table C402.1.2, the *U-factor* of concrete masonry units with integral insulation shall be permitted to be used.

**C402.1.2.1.4 Mass walls and floors.** Compliance with required maximum *U-factors* for mass walls and mass floors in accor- dance with Table C402.1.2 shall be permitted for assemblies complying with Section C402.1.3.4.

**C402.1.2.1.5 Area-weighted averaging of above-grade wall *U*-factors.** Where *above-grade walls* include more than one assembly type or a penetration of the opaque wall area, the area-weighted *U-factor* of the *above-grade wall* is permitted to be determined by an *approved* method.

**C402.1.2.1.6 Cold-formed steel assemblies.** *U*-factors for *building thermal envelopes* containing cold-formed steel-framed ceilings and walls shall be permitted to be determined in accordance with AISI S250 as modified herein.

* 1. Where the steel-framed wall contains no *cavity insulation*, and uses *continuous insulation* to satisfy the *U-factor*

maximum, the steel-framed wall member spacing is permitted to be installed at any on-center spacing.

* 1. Where the steel-framed wall contains framing at 24 inches (610 mm) on center with a 23 percent framing factor or framing at 16 inches (406 mm) on center with a 25 percent framing factor, the next lower framing member spacing input values shall be used when calculating using AISI S250.
  2. Where the steel-framed wall contains less than 23 percent framing factors, the AISI S250 shall be used without any modifications.
  3. Where the steel-framed wall contains other than standard C-shape framing members, the AISI S250 calculation option for other than standard C-shape framing is permitted to be used.

**C402.1.2.1.7 Spandrel panels.** *U-factors* of opaque assemblies within *fenestration* framing systems shall be determined in accordance with the default values in Table C402.1.2.1.7, ASTM C1363 or ANSI/NFRC 100.

|  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE C402.1.2.1.7—EFFECTIVE *U*-FACTORS FOR SPANDREL PANELSa** | | | | | | | | |
| **RATED *R*-VALUE OF INSULATION BETWEEN FRAMING MEMBERS** | | **R-4** | **R-7** | **R-10** | **R-15** | **R-20** | **R-25** | **R-30** |
| **Frame Type** | **Spandrel Panel** | **Default *U*-Factor** | | | | | | |
| Aluminum without thermal breakb | Single glass pane, stone, or metal panel | 0.285 | 0.259 | 0.247 | 0.236 | 0.230 | 0.226 | 0.224 |
| Double glazing with no low-e coatings | 0.273 | 0.254 | 0.244 | 0.234 | 0.229 | 0.226 | 0.223 |
| Triple glazing or double glazing with low-e glass | 0.263 | 0.249 | 0.241 | 0.233 | 0.228 | 0.225 | 0.223 |
| Aluminum with thermal breakc | Single glass pane, stone, or metal panel | 0.243 | 0.212 | 0.197 | 0.184 | 0.176 | 0.172 | 0.169 |
| Double glazing with no low-e coatings | 0.228 | 0.205 | 0.193 | 0.182 | 0.175 | 0.171 | 0.168 |
| Triple glazing or double glazing with low-e glass | 0.217 | 0.199 | 0.189 | 0.180 | 0.174 | 0.170 | 0.167 |
| Structural glazingd | Single glass pane, stone, or metal panel | 0.217 | 0.180 | 0.161 | 0.145 | 0.136 | 0.130 | 0.126 |
| Double glazing with no low-e coatings | 0.199 | 0.172 | 0.157 | 0.143 | 0.135 | 0.129 | 0.126 |
| Triple glazing or double glazing with low-e glass | 0.186 | 0.165 | 0.152 | 0.140 | 0.133 | 0.128 | 0.125 |
| No framing or insulation is continuouse | Single glass pane, stone, or metal panel | 0.160 | 0.108 | 0.082 | 0.058 | 0.045 | 0.037 | 0.031 |
| Double glazing with no low-e coatings | 0.147 | 0.102 | 0.078 | 0.056 | 0.044 | 0.036 | 0.030 |
| Triple glazing or double glazing with low-e glass | 0.139 | 0.098 | 0.076 | 0.055 | 0.043 | 0.035 | 0.030 |
| 1. Extrapolation outside of the table shall not be permitted. Assemblies with distance between framing less than 30 inches, or not included in the default table, shall have a *U*-factor determined by testing in compliance with ASTM C1363 or modeling in compliance with ANSI/NFRC 100. Spandrel panel assemblies in the table do not include metal backpans. For designs with metal backpans, multiply the *U*-factor by 1.2. 2. This frame type shall be used for systems that do not contain a nonmetallic element separating the metal exposed to the exterior from the metal exposed to the interior condition. 3. This frame type shall be used for systems where a nonmetallic element separates the metal exposed to the exterior from the metal that is exposed to the interior condition. 4. This frame type shall be used for systems that have no exposed mullion on the exterior. 5. This frame type shall be used for systems where there is no framing or the insulation is continuous and uninterrupted between framing. | | | | | | | | |

**C402.1.2.1.8 Mechanical equipment penetrations.** Where the total area of through penetrations of mechanical equipment is greater than 1 percent of the opaque above-grade wall area, such area shall be calculated as a separate wall assembly, in accordance with either Section C402.1.2.1.5 or Section C402.1.4 using a published and *approved U-factor* for that equipment or a default *U-factor* of 0.5.

**C402.1.3 Insulation component *R*-value method.** For opaque portions of the *building thermal envelope* the *R*-values for *cavity insulation* and *continuous insulation* shall be not less than that specified in Table C402.1.3. *Group R* occupancy buildings or portions of *commercial buildings* enclosing *Group R* occupancies shall use the *R*-values from the “*Group R*” column of Table C402.1.3. *Commercial buildings* or portions of *commercial buildings* enclosing occupancies other than *Group R* shall use the *R*-values from the “All other” column of Table C402.1.3.

**COMMERCIAL ENERGY EFFICIENCY**

**2024 INTERNATIONAL ENERGY CONSERVATION CODE®**

**73**

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE C402.1.3—OPAQUE BUILDING THERMAL ENVELOPE INSULATION COMPONENT MINIMUM REQUIREMENTS, *R*-VALUE METHODa** | | | | | | | | | | | | | | | | |
| **CLIMATE ZONE** | **0 AND 1** | | **2** | | **3** | | **4 EXCEPT MARINE** | | **5 AND MARINE 4** | | **6** | | **7** | | **8** | |
| **All Other** | **Group R** | **All Other** | **Group R** | **All Other** | **Group R** | **All Other** | **Group R** | **All Other** | **Group R** | **All Other** | **Group R** | **All Other** | **Group R** | **All Other** | **Group R** |
| **Roofs** | | | | | | | | | | | | | | | | |
| Insulation entirely above roof deck | R-20ci | R-25ci | R-25ci | R-25ci | R-25ci | R-25ci | R-30ci | R-30ci | R-30ci | R-30ci | R-30ci | R-30ci | R-35ci | R-35ci | R-35ci | R-35ci |
| Metal buildingsb | R-19 + R-11 LS | R-19 + R-11 LS | R-19 + R11 LS | R-19 + R-11 LS | R-19 + R-11 LS | R-19 + R-11 LS | R-19 + R-11 LS | R-19 + R-11 LS | R-19 + R-11 LS | R-19 + R-11 LS | R-25 + R-11 LS | R-30 + R-11 LS | R-30 + R-11 LS | R-30 + R-11 LS | R-25 + R-11 + R-11 LS | R-25 + R-11 + R-11 LS |
| Attic and other | R-38 | R-38 | R-38 | R-38 | R-38 | R-38 | R-49 | R-49 | R-49 | R-49 | R-49 | R-49 | R-60 | R-60 | R-60 | R-60 |
| **Walls, above grade** | | | | | | | | | | | | | | | | |
| Massf | R-5.7cic | R-5.7cic | R-5.7cic | R-7.6ci | R-7.6ci | R-9.5ci | R-9.5ci | R-11.4ci | R-11.4ci | R-13.3ci | R-13.3ci | R-15.2ci | R-15.2ci | R-15.2ci | R-25ci | R-25ci |
| Metal building | R-13 + R-6.5ci | R-13 + R-6.5ci | R13 + R-6.5ci | R-13 +  R-13ci | R-13 + R-6.5ci | R-13 +  R-13ci | R-13 +  R-13ci | R-13 +  R-14ci | R-13 +  R-14ci | R-13 +  R-14ci | R-13 +  R-14ci | R-13 +  R-14ci | R-13 +  R-17ci | R-13 + R-19.5ci | R-13 + R-19.5ci | R-13 + R-19.5ci |
| Metal framedh, i | R-0 +  R-10ci or R-13 +  R-5ci or R-20 + R-3.8ci | R-0 +  R-10ci or R-13 +  R-5ci or R-20 + R-3.8ci | R-0 +  R-10ci or R-13 +  R-5ci or R-20 + R-3.8ci | R-0 +  R-12.6ci or R-13 +  R-7.5ci or R-20 +  R-6.3ci | R-0 +  R-12.6ci or R-13 +  R-7.5ci or R-20 +  R-6.3ci | R-0 +  R-12.6ci or R-13 +  R-7.5ci or R-20 +  R-6.3ci | R-0 +  R-12.6ci or R-13 +  R-7.5ci or R-20 +  R-6.3ci | R-0 +  R-12.6ci or R-13 +  R-7.5ci or R-20 +  R-6.3ci | R-0 +  R-15.2ci or R-13 +  R-10ci or R-20 +  R-9ci | R-0 +  R-15.2ci or R-13 +  R-10ci or R-20 +  R-9ci | R-0 +  R-17.3ci or R-13 +  R-12.5ci or R-20 +  R-11ci | R-0 +  R-17.3ci or R-13 +  R-12.5ci or R-20 +  R-11ci | R-0 +  R-17.3ci or R-13 +  R-12.5ci or R-20 +  R-11ci | R-0 +  R-21ci or R-13 +  R-15.6ci or R-20 +  R-14.3ci | R-0 +  R-24ci or R-13 +  R-18.8ci or R-20 +  R-17.5ci | R-0 +  R-24ci or R-13 +  R-18.8ci or R-20 +  R-17.5ci |
| Wood framed and otherh, i | R-0 +  R-12ci or R-13 +  R-3.8ci or R-20 | R-0 +  R-12ci or R-13 +  R-3.8ci or R-20 | R-0 +  R-12ci or R-13 +  R-3.8ci or R-20 | R-0 +  R-12ci or R-13 +  R-3.8ci or R-20 | R-0 +  R-12ci or R-13 +  R-3.8ci or R-20 | R-0 +  R-12ci or R-13 +  R-3.8ci or R-20 | R-0 +  R-12ci or R-13 +  R-3.8ci or R-20 | R-0 +  R-12ci or R-13 +  R-3.8ci or R-20 | R-0 +  R-16ci or R-13 +  R-7.5ci or R20 +  R3.8ci or R-27 | R-0 +  R-16ci or R-13 +  R-7.5ci or R-20 +  R-3.8ci or R-27 | R-0 +  R-16ci or R-13 +  R-7.5ci or R-20 +  R-3.8ci or R-27 | R-0 +  R-16ci or R-13 +  R-7.5ci or R-20 +  R-3.8ci or R-27 | R-0 +  R-16ci or R-13 +  R-7.5ci or R-20 +  R-3.8ci or R-27 | R-0 +  R-16ci or R-13 +  R-7.5ci or R-20 +  R-3.8ci or R-27 | R-0 +  R-27.5ci or R-13 +  R-18.8ci or R-20 +  R-14ci | R-0 +  R-27.5ci or R-13 +  R-18.8ci or R-20 +  R-14ci |
| **Walls, below grade** | | | | | | | | | | | | | | | | |
| Below-grade walld | NR | NR | NR | NR | NR | NR | R-7.5ci | R-10ci | R-7.5ci | R-10ci | R-10ci | R-15ci | R-15ci | R-15ci | R-15ci | R-15ci |
| **Floors** | | | | | | | | | | | | | | | | |
| Masse | NR | NR | R-6.3ci | R-8.3ci | R-10ci | R-10ci | R-14.6ci | R-16.7ci | R-14.6ci | R-16.7ci | R-16.7ci | R-16.7ci | R-20.9ci | R-20.9ci | R-23ci | R-23ci |
| Joist/framing | R-13 | R-13 | R-30 | R-30 | R-30 | R-30 | R-30 | R-30 | R-30 | R-30 | R-38 | R-38 | R-38 | R-38 | R-38 | R-38 |
| **Slab-on-grade floors** | | | | | | | | | | | | | | | | |
| Unheated slabs | NR | NR | NR | NR | NR | R-10 for 24″ below | R-15 for 24″ below | R-15 for 24″ below | R-15 for 24″ below | R-20 for 24″ below | R-20 for 24″ below | R-20 for 48″ below | R-20 for 24″ below | R-20 for 48″ below | R-20 for 48″ below | R-25 for 48″ below |
| Heated slabsg | R-7.5 for 12″ below  + R-5 full slab | R-7.5 for 12″ below  + R-5 full slab | R-7.5 for 12″ below  + R-5 full slab | R-7.5 for 12″ below  + R-5 full slab | R-10 for 24″ below  + R-5 full slab | R-10 for 24″ below  + R-5 full slab | R-15 for 24″ below  + R-5 full slab | R-15 for 24″ below  + R-5 full slab | R-15 for 36″ below  + R-5 full slab | R-15 for 36″ below  + R-5 full slab | R-15 for 36″ below  + R-5 full slab | R-20 for 48″ below  + R-5 full slab | R-20 for 48″ below  + R-5 full slab | R-20 for 48″ below  + R-5 full slab | R-20 for 48″ below  + R-5 full slab | R-20 for 48″ below  + R-5 full slab |

**COMMERCIAL ENERGY EFFICIENCY**

**74**

**2024 INTERNATIONAL ENERGY CONSERVATION CODE®**

For SI: 1 inch = 25.4 mm, 1 pound per square foot = 4.88 kg/m2, 1 pound per cubic foot = 16 kg/m3. ci = Continuous Insulation, NR = No Requirement, LS = Liner System.

1. Assembly descriptions can be found in ANSI/ASHRAE/IES 90.1 Appendix A.
2. Where using *R*-value compliance method, a thermal spacer block shall be provided, otherwise use the *U*-factor compliance method in Table C402.1.2.
3. R-5.7ci is allowed to be substituted with concrete block walls complying with ASTM C90, ungrouted or partially grouted not less than 32 inches on center vertically and not less than 48 inches on center horizontally, with ungrouted cores filled with materials having a maximum thermal conductivity of 0.44 Btu-in/h-ft2°F.
4. Where heated slabs are below grade, below-grade walls shall comply with the *R*-value requirements for above-grade mass walls.
5. “Mass floors” shall be in accordance with Section C402.1.3.4.
6. “Mass walls” shall be in accordance with Section C402.1.3.4.
7. The first value is for perimeter insulation and the second value is for full, under-slab insulation. Perimeter insulation and full-slab insulation components shall be installed in accordance with Section C402.2.4.
8. The first value is cavity insulation; the second value is continuous insulation. Therefore, “R-0 + R-12ci” means R-12 continuous insulation and no cavity insulation; “R-13 + R-3.8ci” means R-13 cavity insulation and R-3.8 continuous insu- lation; “R-20” means R-20 cavity insulation and no continuous insulation. R-13, R-20 and R-27 cavity insulation, as used in this table, apply to a nominal 4-inch, 6-inch and 8-inch-deep wood or cold-formed steel stud cavities, respectively.
9. Where the required *R*-value in Table C402.1.3 is met by using continuous insulation such that cavity insulation is not required, the *R*-value is applicable to any wall framing spacing.

**TABLE C402.1.3—OPAQUE THERMAL ENVELOPE INSULATION COMPONENT MINIMUM REQUIREMENTS, *R*-VALUE METHODa—continued**

**C402.1.3.1 *R*-value of multi-layered insulation components.** Where *cavity insulation* is installed in multiple layers, the *cavity insulation R*-values shall be summed to determine compliance with the *cavity insulation R-value* requirements. Where *continu- ous insulation* is installed in multiple layers, the *continuous insulation R*-values shall be summed to determine compliance with the *continuous insulation R-value* requirements. *Cavity insulation R*-values shall not be used to determine compliance with the *continuous insulation R-value* requirements in Table C402.1.3.

**C402.1.3.2 Area-weighted averaging of *R*-values.** Area-weighted averaging shall not be permitted for *R-value* compliance.

**Exception:** For tapered above-deck roof insulation, compliance with the *R*-values required in Table C402.1.3 shall be permit- ted to be demonstrated by multiplying the rated *R-value* per inch of the insulation material by the average thickness of the roof insulation. The average thickness of the roof insulation shall equal the total volume of the roof insulation divided by the area of the roof.

**C402.1.3.3 Suspended ceilings.** Insulation installed on suspended ceilings having removable ceiling tiles shall not be consid- ered part of the minimum thermal resistance (*R-value*) of roof insulation in roof-ceiling construction.

**C402.1.3.4 Mass walls and mass floors.** Compliance with required maximum *U-factors* for mass walls and mass floors in accordance with Table C402.1.2 and minimum *R*-values for insulation components applied to mass walls and mass floors in accordance with Table C402.1.3 shall be permitted for assemblies complying with the following:

1. Where used as a component of the *building thermal envelope*, mass walls shall comply with one of the following:
   1. Weigh not less that 35 pounds per square foot (171 kg/m2) of wall surface area.
   2. Weigh not less than 25 pounds per square foot (122 kg/m2 ) of wall surface area where the material weight is not more than 120 pounds per cubic foot (pcf) (1922 kg/m3).
   3. Have a heat capacity exceeding 7 Btu/ft2 × °F (144 kJ/m2 × K).
   4. Have a heat capacity exceeding 5 Btu/ft2 × °F (103 kJ/m2 × K) where the material weight is not more than 120 pcf (1922 kg/m3).
2. Where used as a component of the *building thermal envelope*, the minimum weight of mass floors shall comply with one of the following:
   1. Thirty-five pounds per square foot (171 kg/m2) of floor surface area.
   2. Twenty-five pounds per square foot (122 kg/m2) of floor surface area where the material weight is not more than 120 pcf (1922 kg/m3).

**C402.1.4 Component performance method.** *Building thermal envelope* values and *fenestration* areas determined in accordance with Equation 4-1 shall be an alternative to compliance with the *U-*, *F*-, psi-, chi-, and *C*-factors in Tables C402.1.2, C402.1.2.1.7, C402.1.4 and C402.5 and the maximum allowable *fenestration* areas in Section C402.5.1. *Fenestration* shall meet the applicable SHGC requirements of Section C402.5.3.

**Equation 4-1** *AP* + *BP* + *CP* + *TP*  *AT* + *BT* + *CT* + *TT* - *VF* - *VS*

where:

*AP* = Sum of the (area × *U*-factor) for each proposed building thermal envelope assembly, other than slab-on-grade or below-grade wall assemblies.

*BP* = Sum of the (length × *F*-factor) for each proposed slab-on-grade edge condition.

*CP* = Sum of the (area × *C*-factor) for each proposed below-grade wall assembly.

*TP* = Sum of the (*LP*) and (*NP*) values for each type of thermal bridge condition of the building thermal envelope as identified in Section C402.7 in the proposed building. For the purposes of this section, the (*LP*) and (*NP*) values for ther- mal bridges caused by materials with a thermal conductivity less than or equal to 3.0 Btu × in/h × ft2 × °F shall be assigned as zero. For buildings or structures located in Climate Zones 0 through 3, the value of *TP* shall be assigned as zero.

*LP* = Psi-factor × length of the thermal bridge elements in the proposed building thermal envelope.

*NP* = Chi-factor × number of the thermal bridge point elements other than fasteners, ties or brackets in the proposed building thermal envelope.

*AT* = Sum of the (area × *U*-factor permitted by Tables C402.1.2 and C402.5) for each proposed building thermal envelope assembly, other than slab-on-grade or below-grade wall assemblies.

*BT* = Sum of the (length × *F*-factor permitted by Table C402.1.2) for each proposed slab-on-grade edge condition.

*CT* = Sum of the (area × *C*-factor permitted by Table C402.1.2) for each proposed below-grade wall assembly.

*TT* = Sum of the (*LT*) and (*NT*) values for each type of thermal bridge condition in the proposed building thermal enve- lope as identified in Section C402.7 with values specified as “compliant” in Table C402.1.4. For the purposes of this section, the (*LT*) and (*NT*) values for thermal bridges caused by materials with a thermal conductivity less than or equal to 3.0 Btu × in/h × ft2 × °F shall be assigned as zero. For buildings or structures located in Climate Zones 0 through 3, the value of *TT* shall be assigned as zero.

*LT* = (Psi-factor specified as “compliant” in Table C402.1.4) × length of the thermal bridge elements in the proposed building thermal envelope.

*NT* = (Chi-factor specified as “compliant” in Table C402.1.4) × number of the thermal bridge point elements other than fasteners, ties or brackets in the proposed building thermal envelope.

*PF* = Maximum vertical fenestration area allowable by Section C402.5.1, C402.5.1.1 or C402.5.1.2.

*QF* = Proposed vertical fenestration area.

*RF* = *QF* – *PF*, but not less than zero (excess vertical fenestration area).

*SF* = Area-weighted average *U*-factor permitted by Table C402.5 of all vertical fenestration assemblies. *TF* = Area-weighted average *U*-factor permitted by Table C402.1.2 of all exterior opaque wall assemblies. *UF* = *SF* – *TF* (excess *U*-factor for excess vertical fenestration area).

*VF* = *RF* × *UF* (excess *U* × *A* due to excess vertical fenestration area).

*PS* = Maximum skylight area allowable by Section C402.1.2.

*QS* = Actual skylight area.

*RS* = *QS* – *PS*, but not less than zero (excess skylight area).

*SS* = Area-weighted average *U*-factor permitted by Table C402.5 of all skylights.

*TS* = Area-weighted average *U*-factor permitted by Table C402.1.2 of all opaque roof assemblies.

*US* = *SS* – *TS* (excess *U*-factor for excess skylight area).

*VS* = *RS* × *US* (excess *U* × *A* due to excess skylight area).

A proposed psi- or *chi-factor* for each thermal bridge shall comply with one of the following, as applicable:

1. Where the proposed mitigation of a thermal bridge is compliant with the requirements of Section C402.7, the “compliant” values in Table C402.1.4 shall be used for the proposed psi- or chi-factors.
2. Where a thermal bridge is not mitigated in a manner at least equivalent to Section C402.7, the “noncompli- ant” values in Table C402.1.4 shall be used for the proposed psi- or chi-factors.
3. Where the proposed mitigation of a thermal bridge provides a psi- or chi-factor less than the “compliant” values in Table C402.1.4, the proposed psi- or chi-factor shall be determined by thermal analysis, testing or other approved sources.

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **TABLE C402.1.4—PSI- and CHI-FACTORS TO DETERMINE THERMAL BRIDGES FOR THE COMPONENT PERFORMANCE METHOD** | | | | |
| **THERMAL BRIDGE PER SECTION C402.7** | **THERMAL BRIDGE COMPLIANT WITH SECTION C402.7** | | **THERMAL BRIDGE NONCOMPLIANT WITH SECTION C402.7** | |
|  | **Psi-Factor (Btu/h × ft × °F)** | **Chi-Factor (Btu/h × °F)** | **Psi-Factor (Btu/h × ft × °F)** | **Chi-Factor (Btu/h × °F)** |
| C402.7.1 Balconies and floor decks | 0.2 | N/A | 0.5 | N/A |
| C402.7.2 Cladding supports | 0.2 | N/A | 0.3 | N/A |
| C402.7.3 Structural beams and columns | N/A | 1.0 carbon steel  0.3 concrete | N/A | 2.0 carbon steel  1.0 concrete |
| C402.7.4 Vertical fenestration | 0.15 | N/A | 0.3 | N/A |
| C402.7.5 Parapets | 0.2 | N/A | 0.4 | N/A |
| For SI: 1 W/m × K = 0.578 Btu/h × ft × °F, 1 W/K = 1.9 Btu/h × °F. N/A = Not Applicable. | | | | |

**C402.1.5 Rooms containing fuel-burning appliances.** In Climate Zones 3 through 8, where combustion air is supplied through open- ings in an *exterior wall* to a room or space containing a space-conditioning fuel-burning appliance, one of the following shall apply:

1. The room or space containing the appliance shall be located outside of the *building thermal envelope*.
2. The room or space containing the appliance shall be enclosed and isolated from *conditioned spaces* inside the *building thermal envelope*. Such rooms shall comply with all of the following:
   1. The walls, floors and ceilings that separate the enclosed room or space from *conditioned spaces* shall be insu- lated to be not less than equivalent to the insulation requirement of *below-grade walls* as specified in Table C402.1.3 or Table C402.1.2.
   2. The walls, floors and ceilings that separate the enclosed room or space from *conditioned spaces* shall be sealed in accordance with Section C402.6.1.2.
   3. The doors into the enclosed room or space shall be fully gasketed.
   4. Piping serving as part of a heating or cooling system and *ducts* in the enclosed room or space shall be insulated in accordance with Section C403. Service water piping shall be insulated in accordance with Section C404.
   5. Where an air *duct* supplying combustion air to the enclosed room or space passes through *conditioned space*, the *duct* shall be insulated to an *R-value* of not less than R-8.

**Exception:** Fireplaces and stoves complying with Sections 901 through 905 of the *International Mechanical Code*, and Section 2111.14 of the *International Building Code*.

**C402.2 Specific insulation and installation requirements.** Insulation in *building thermal envelope* opaque assemblies shall be installed in accordance with Section C303.2 and Sections C402.2.1 through C402.2.7, or an *approved* design.

**C402.2.1 Roof-ceiling construction.** Insulation materials in the roof-ceiling construction shall be installed between the roof or ceiling framing, continuously below the ceiling framing, continuously above, below, or within the roof deck or in any *approved* combination thereof. Insulation installed above the roof deck shall comply with Sections C402.2.1.1 through C402.2.1.3.

**C402.2.1.1 Joints staggered.** Continuous, above-deck insulation board located above the roof deck shall be installed in not less than two layers and the edge joints between each layer of insulation shall be staggered, except where insulation tapers to the roof deck at a gutter edge, roof drain or scupper.

**C402.2.1.2 Skylight curbs.** Skylight curbs shall be insulated to the level of the above-deck roof insulation or R-5, whichever is less.

**Exception:** Unit skylight curbs included as a component of a skylight *listed* and *labeled* in accordance with NFRC 100 shall not be required to be insulated.

**C402.2.1.3 Minimum thickness of tapered insulation.** The thickness of tapered above-deck roof insulation at its lowest point, gutter edge, roof drain or scupper, shall be not less than 1 inch (25 mm).

**C402.2.2 Above-grade walls.** *Above-grade wall* insulation materials shall be installed between the wall framing, be integral to the wall assembly, be continuous on the wall assembly, or be any combination of these insulation methods. Where *continuous insulation* is layered on the exterior side of a wall assembly, the joints shall be staggered.

**C402.2.3 Floors over outdoor air or unconditioned space.** Floor insulation shall be installed between floor framing, be integral to the floor assembly, be continuous on the floor assembly, or be any combination of these insulation methods. Where *continuous insulation* is layered on the exterior side of a floor assembly, the joints shall be staggered. Floor framing *cavity insulation* or struc- tural slab insulation shall be installed to maintain permanent contact with the underside of the subfloor decking or structural slabs.

Exceptions:

1. The floor framing *cavity insulation* or structural slab insulation shall be permitted to be installed in contact with the top side of sheathing or *continuous insulation* installed on the bottom side of floor assemblies. Floor framing or struc- tural slab members at the perimeter of the floor assembly shall be insulated vertically for their full depth with insulation equivalent to that required for the *above-grade wall* construction.
2. Insulation applied to the underside of concrete floor slabs shall be permitted an airspace of not more than 1 inch (25 mm) where it turns up and is in contact with the underside of the floor under walls associated with the *building ther- mal envelope*.

**C402.2.4 Slabs-on-grade.** Where installed, the perimeter insulation for slab-on-grade shall be placed on the outside of the foun- dation or on the inside of the foundation wall. For installations complying with Table C402.1.3, the perimeter insulation shall extend downward from the top of the slab for the minimum distance shown in the table or to the top of the footing, whichever is less, or downward to not less than the bottom of the slab and then horizontally to the interior or exterior for the total distance shown in the table. Where installed, full slab insulation shall be continuous under the entire area of the slab-on-grade floor, except at structural column locations and service penetrations. Insulation required at the *heated slab* perimeter shall not be required to extend below the bottom of the heated slab and shall be continuous with the full slab insulation.

**Exception:** Where the slab-on-grade floor is greater than 24 inches (610 mm) below the finished exterior grade, perimeter insu- lation is not required.

**C402.2.5 Below-grade walls.** Below-grade wall insulation shall be installed between framing members, be integral to the wall assembly, be continuous on the wall assembly, or be any combination of these insulation methods. For installations complying with Section C401.2.1, insulation shall extend to a depth of not less than 10 feet (3048 mm) below the outside finished ground level or to the level of the lowest floor of the *conditioned space* enclosed by the *below-grade wall*, whichever is less.

**C402.2.6 Insulation of radiant heating system panels.** *Radiant heating system* panels, and their associated components that are installed in interior or exterior assemblies, shall be insulated to an *R*-value of not less than R*-*3.5 on all surfaces not facing the space being heated. *Radiant heating system* panels that are installed in the *building thermal envelope* shall be separated from the exterior of the building or unconditioned or exempt spaces by not less than the *R*-value of insulation installed in the opaque assembly in which they are installed or the assembly shall comply with Section C402.1.2.

**C402.2.7 Airspaces.** Where the *R-value* of an airspace is used for compliance in accordance with Section C402.1, the airspace shall be enclosed in a cavity bounded on all sides by building components and constructed to minimize airflow into and out of the enclosed airspace. Airflow shall be deemed minimized where one of the following conditions occur:

1. The enclosed airspace is unventilated.
2. The enclosed airspace is bounded on at least one side by an anchored masonry veneer, constructed in accordance with Chapter 14 of the *International Building Code* and vented by veneer weep holes located only at the bottom of the airspace and spaced not less than 15 inches (381 mm) on center with top of the cavity airspace closed.

**Exception:** For ventilated cavities, the effect of the *ventilation* of airspaces located on the exterior side of the continuous *air barrier* and adjacent to and behind the exterior wall-covering material shall be determined in accordance with ASTM C1363 modified with an airflow entering the bottom and exiting the top of the airspace at an air movement rate of not less than 70 mm/second.

**C402.3 Above-grade wall solar reflectance.** For Climate Zone 0, above-grade *east-oriented*, *south-oriented* and *west-oriented* walls shall comply with either of the following:

1. Not less than 75 percent of the opaque *above-grade wall* area shall have an area-weighted initial solar reflectance of not less than 0.30 where tested in accordance with ASTM C1549 with AM1.5GV output or ASTM E903 with AM1.5GV output, or determined in accordance with an *approved source*. This *above-grade wall* area shall have an *emittance* or emissivity of not less than 0.75 where tested in accordance with ASTM C835, ASTM C1371, ASTM E408 or determined in accordance with an *approved source*. For the portion of the *above-grade wall* that is glass spandrel area, a solar reflectance of not less than 0.29, as determined in accordance with NFRC 300 or ISO 9050, shall be permitted. Area-weighted averaging is permitted using only *south-*, *east-* and *west-oriented* walls enclosing the same occupancy classification.
2. Not less than 30 percent of the opaque *above-grade wall* area shall be shaded by manmade structures, existing buildings, hillsides, permanent building projections, *on-site renewable energy* systems or a combination of these. Shade coverage shall be calculated by projecting the shading surface downward on the *above-grade wall* at an angle of 45 degrees.

**Exception:** *Above-grade walls* of low-energy buildings complying with Section C402.1.1.1, greenhouses complying with Section C402.1.1.2 and equipment buildings complying with Section C402.1.1.3.

**C402.4 Roof solar reflectance and thermal emittance.** *Low slope* roofs directly above cooled *conditioned spaces* in Climate Zones 0 through 3 shall comply with one or more of the options in Table C402.4.

**Exceptions:** The following roofs and portions of roofs are exempt from the requirements of Table C402.4:

* 1. Portions of the roof that include or are covered by the following:
     1. Photovoltaic systems or components.
     2. Solar air or water-heating systems or components.
     3. *Vegetative roofs* or landscaped roofs.
     4. Above-roof decks or walkways.
     5. Skylights.
     6. HVAC systems and components, and other opaque objects mounted above the roof.
  2. Portions of the roof shaded during the peak sun angle on the summer solstice by permanent features of the *building* or by permanent features of adjacent buildings.
  3. Portions of roofs that are ballasted with a minimum stone ballast of 17 pounds per square foot (74 kg/m2) or 23 psf (117 kg/m2) pavers.
  4. Roofs where not less than 75 percent of the roof area complies with one or more of the exceptions to this section.

|  |
| --- |
| **TABLE C402.4—MINIMUM ROOF REFLECTANCE AND EMITTANCE OPTIONSa** |
| Three-year-aged solar reflectanceb of 0.55 and 3-year aged thermal emittancec of 0.75 |
| Three-year-aged solar reflectance indexd of 64 |
| 1. The use of area-weighted averages to comply with these requirements shall be permitted. Materials lacking 3-year-aged tested values for either solar reflectance or thermal emittance shall be assigned both a 3-year-aged solar reflectance in accordance with Section C402.4.1 and a 3-year-aged thermal emittance of 0.90. 2. Aged solar reflectance tested in accordance with ASTM C1549, ASTM E903 or ASTM E1918 or CRRC-S100. 3. Aged thermal emittance tested in accordance with ASTM C1371 or ASTM E408 or CRRC-S100. 4. Solar reflectance index (SRI) shall be determined in accordance with ASTM E1980 using a convection coefficient of 2.1 Btu/h × ft2 × °F (12 W/m2 × K). Calculation of aged SRI shall be based on aged tested values of solar reflectance and thermal emittance. |

**C402.4.1 Aged roof solar reflectance.** Where an aged solar reflectance required by Section C402.4 is not available, it shall be determined in accordance with Equation 4-2.

**Equation 4-2** *Raged* = [0.2 + 0.7(*Rinitial* – 0.2)] where:

*Raged* = The aged solar reflectance.

*Rinitial* = The initial solar reflectance determined in accordance with CRRC-S100.

**C402.5 Fenestration.** *Fenestration* shall comply with Sections C402.5.1 through C402.5.5 and Table C402.5. *Daylight responsive controls* shall comply with this section and Section C405.2.4.

**COMMERCIAL ENERGY EFFICIENCY**

**2024 INTERNATIONAL ENERGY CONSERVATION CODE®**

**79**

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE C402.5—BUILDING THERMAL ENVELOPE FENESTRATION MAXIMUM *U*-FACTOR AND SHGC REQUIREMENTS** | | | | | | | | | | | | | | | | |
| **CLIMATE ZONE** | **0 AND 1** | | **2** | | **3** | | **4 EXCEPT MARINE** | | **5 AND MARINE 4** | | **6** | | **7** | | **8** | |
| **Vertical fenestration** | | | | | | | | | | | | | | | | |
| ***U*-factor** | | | | | | | | | | | | | | | | |
| Fixed fenestration | 0.50 | | 0.45 | | 0.38 | | 0.34 | | 0.34 | | 0.34 | | 0.28 | | 0.25 | |
| Operable fenestration | 0.62 | | 0.60 | | 0.54 | | 0.45 | | 0.45 | | 0.42 | | 0.36 | | 0.32 | |
| Entrance doors | 0.83 | | 0.77 | | 0.68 | | 0.63 | | 0.63 | | 0.63 | | 0.63 | | 0.63 | |
| **SHGC** | | | | | | | | | | | | | | | | |
|  | Fixed | Operable | Fixed | Operable | Fixed | Operable | Fixed | Operable | Fixed | Operable | Fixed | Operable | Fixed | Operable | Fixed | Operable |
| PF < 0.2 | 0.23 | 0.21 | 0.25 | 0.23 | 0.25 | 0.23 | 0.36 | 0.33 | 0.38 | 0.33 | 0.38 | 0.34 | 0.40 | 0.36 | 0.40 | 0.36 |
| 0.2 ≤ PF < 0.5 | 0.28 | 0.25 | 0.30 | 0.28 | 0.30 | 0.28 | 0.43 | 0.40 | 0.46 | 0.40 | 0.46 | 0.41 | 0.48 | 0.43 | 0.48 | 0.43 |
| PF ≥ 0.5 | 0.37 | 0.34 | 0.40 | 0.37 | 0.40 | 0.37 | 0.58 | 0.53 | 0.61 | 0.53 | 0.61 | 0.54 | 0.64 | 0.58 | 0.64 | 0.58 |
| **Skylights** | | | | | | | | | | | | | | | | |
| *U*-factor | 0.70 | | 0.65 | | 0.55 | | 0.50 | | 0.50 | | 0.50 | | 0.44 | | 0.41 | |
| SHGC | 0.30 | | 0.30 | | 0.30 | | 0.40 | | 0.40 | | 0.40 | | NR | | NR | |
| NR = No Requirement, PF = Projection Factor. | | | | | | | | | | | | | | | | |

**C402.5.1 Maximum area.** The vertical *fenestration* area, not including *opaque doors* and opaque spandrel panels, shall be not greater than 30 percent of the gross *above-grade wall* area. The skylight area shall be not greater than 3 percent of the gross roof area.

**C402.5.1.1 Increased vertical fenestration area with daylight responsive controls.** In Climate Zones 0 through 6, not more than 40 percent of the gross *above-grade wall* area shall be vertical *fenestration*, provided that all of the following requirements are met:

1. In buildings not greater than two stories above grade, not less than 50 percent of the *net floor area* is within a primary sidelit *daylight zone* or a toplit *daylight zone*.
2. In buildings three or more stories above grade, not less than 25 percent of the *net floor area* is within a primary sidelit

*daylight zone* or a toplit *daylight zone*.

1. *Daylight responsive controls* are installed in *daylight zones.*
2. *Visible transmittance* (VT) of vertical *fenestration* is not less than 1.1 times *solar heat gain coefficient* (SHGC).

**Exception:** *Fenestration* that is outside the scope of NFRC 200 is not required to comply with Item 4.

**C402.5.1.2 Increased skylight area with daylight responsive controls.** The skylight area shall be not more than 6 percent of the roof area provided that *daylight responsive controls* are installed in toplit *daylight zones*.

**C402.5.1.3 Fenestration orientation.** The vertical *fenestration* shall comply with either Equation a or b:

1. AW ≤ (AT)/4 and AE ≤ (AT)/4
2. AW × SHGCW ≤ (AT × SHGCC)/5 and AE × SHGCE ≤ (AT × SHGCC)/5

where:

AW = West-oriented *vertical fenestration area* (oriented within 45 degrees of true west tothe south and within 22.5

degrees of truewest to the north in the NorthernHemisphere).

AE = East-oriented *vertical fenestration area* (oriented within 45 degrees of true east tothe south and within 22.5

degrees of trueeast to the north in the NorthernHemisphere).

AT= Total vertical fenestration area.

SHGCC = SHGC criteria in Table C402.5.

SHGCE = SHGC for east-oriented fenestration.

SHGCW = SHGC for west-oriented fenestration.

**Exceptions:**

1. Buildings with shade on 75 percent of the east-oriented and west-oriented vertical fenestration areas from permanent projections, existing buildings, existing permanent infrastructure or topography at 9:00 a.m. and 3:00 p.m., respectively, on the summer solstice (June 21).
2. Alterations and additions with no increase in vertical fenestration area.
3. Buildings where the east-oriented and west-oriented vertical fenestration area does not exceed 20 percent of the gross wall area for each of those facades, and SHGC on those facades is no greater than 90 percent of the criteria in Table C402.5.

**C402.5.2 Minimum skylight fenestration area.** Skylights shall be provided in *enclosed spaces* greater than 2,500 square feet (232 m2) in floor area, directly under a roof with not less than 75 percent of the ceiling area with a ceiling height greater than 15 feet (4572 mm), and used as an office, lobby, atrium, concourse, corridor, storage space, gymnasium/exercise center, convention center, automotive service area, space where manufacturing occurs, nonrefrigerated warehouse, retail store, distribution/sorting area, transportation depot or workshop. The total *toplit daylight zone* shall be not less than half the floor area and shall comply with one of the following:

1. A minimum skylight area to toplit *daylight zone* of not less than 3 percent where all skylights have a VT of not less than 0.40, or VTannual of not less than 0.26, as determined in accordance with Section C303.1.3.
2. A minimum skylight effective aperture, determined in accordance with Equation 4-3, of:
   1. Not less than 1 percent using a skylight’s VT rating; or
   2. Not less than 0.66 percent using a Tubular Daylight Device’s VTannual rating.

Equation 4-3

where:

Skylight Effective Aperture =

-0---.-8---5----×----S----k---y---l--i-g----h---t----A---r--e---a-----×-----S---k---y---l--i-g----h--t----V--T-----×----W F--

Toplit Zone

Skylight area = Total fenestration area of skylights.

Skylight VT = Area-weighted average visible transmittance of skylights.

WF = Area-weighted average well factor, where well factor is 0.9 if light well depth is less than 2 feet (610 mm), or 0.7 if light well depth is 2 feet (610 mm) or greater, or 1.0 for Tubular Daylighting Devices with VTannual ratings.

Light well depth = Measure vertically from the underside of the lowest point of the skylight glazing to the ceiling plane under the skylight.

**Exceptions:** Skylights above *daylight zones* of *enclosed spaces* are not required in:

1. Buildings in *Climate Zones* 6 through 8.
2. Spaces where the designed *general lighting* power densities are less than 0.5 W/ft2 (5.4 W/m2).
3. Areas where it is documented that existing structures or natural objects block direct beam sunlight on not less than half of the roof over the enclosed area for more than 1,500 daytime hours per year between 8 a.m. and 4 p.m.
4. Spaces where the *daylight zone* under rooftop monitors is greater than 50 percent of the *enclosed space* floor area.
5. Spaces where the total area minus the area of *sidelit daylight zones* is less than 2,500 square feet (232 m2), and where the lighting is controlled in accordance with Section C405.2.3.
6. Spaces designed as storm shelters complying with ICC 500.

**C402.5.2.1 Lighting controls in toplit daylight zones.** *Daylight responsive controls* shall be provided in toplit *daylight zones*.

**C402.5.2.2 Haze factor.** Skylights in office, storage, automotive service, manufacturing, nonrefrigerated warehouse, retail store and distribution/sorting area spaces shall have a glazing material or diffuser with a haze factor greater than 90 percent when tested in accordance with ASTM D1003.

**Exception:** Skylights and tubular daylighting devices designed and installed to exclude direct sunlight entering the occupied space by the use of fixed or automated baffles, the geometry of skylight and light well or the use of optical diffuser components.

**C402.5.3 Maximum *U*-factor and SHGC.** The maximum *U-factor* and *solar heat gain coefficient* (SHGC) for *fenestration* shall be as specified in Table C402.5.

The window projection factor shall be determined in accordance with Equation 4-4.

**Equation 4-4** *PF* = *A/B*

where:

*PF* = Projection factor (decimal).

*A* = Distance measured horizontally from the farthest continuous extremity of any overhang, eave or permanently attached shading device to the vertical surface of the glazing.

*B* = Distance measured vertically from the bottom of the glazing to the underside of the overhang, eave or permanently attached shading device.

Where different windows or glass doors have different *PF* values, they shall each be evaluated separately.

**C402.5.3.1 Increased skylight SHGC.** In Climate Zones 0 through 6, skylights shall be permitted a maximum SHGC of 0.60 where located above *daylight zones* provided with *daylight responsive controls*.

**C402.5.3.2 Increased skylight *U-*factor.** Where skylights are installed above *daylight zones* provided with *daylight responsive controls*, a maximum *U-factor* of 0.9 shall be permitted in Climate Zones 0 through 3 and a maximum *U-factor* of 0.75 shall be permitted in *Climate Zones* 4 through 8.

**C402.5.3.3 Dynamic glazing.** Where *dynamic glazing* is intended to satisfy the SHGC and VT requirements of Table C402.5, the ratio of the higher to lower *labeled* SHGC shall be greater than or equal to 2.4, and the *dynamic glazing* shall be automatically controlled to modulate the amount of solar gain into the space in multiple steps. *Dynamic glazing* shall be considered separately from other *fenestration*, and area-weighted averaging with other *fenestration* that is not *dynamic glazing* shall not be permitted.

**Exception:** *Dynamic glazing* is not required to comply with this section where both the lower and higher *labeled* SHGC already comply with the requirements of Table C402.5.

**C402.5.3.4 Area-weighted *U*-factor.** An area-weighted average shall be permitted to satisfy the *U-factor* requirements for each *fenestration* product category listed in Table C402.5. Individual *fenestration* products from different *fenestration* product categories listed in Table C402.5 shall not be combined in calculating area-weighted average *U-factor*.

**C402.5.4 Daylight zones.** *Daylight zones* referenced in Sections C402.5.1.1 through C402.5.3.2 shall comply with Sections C405.2.4.2 and C405.2.4.3, as applicable. *Daylight zones* shall include toplit *daylight zones* and sidelit *daylight* zones.

**C402.5.5 Doors.** Opaque swinging doors shall comply with Table C402.1.2. Opaque nonswinging doors shall comply with Table C402.1.2. *Opaque doors* shall be considered as part of the gross area of *above-grade walls* that are part of the *building thermal envelope*. *Opaque doors* shall comply with Section C402.5.5.1 or C402.5.5.2. Other doors shall comply with the provisions of Section C402.5.3 for vertical *fenestration*.

**C402.5.5.1 Opaque swinging doors.** Opaque swinging doors shall comply with Table C402.1.2.

**C402.5.5.2 Nonswinging doors.** Opaque nonswinging doors that are horizontally hinged sectional doors with a single row of

*fenestration* shall have an assembly *U-factor* less than or equal to 0.440 in Climate Zones 0 through 6 and less than or equal to

0.360 in Climate Zones 7 and 8, provided that the *fenestration* area is not less than 14 percent and not more than 25 percent of the total door area.

**Exception:** Other doors shall comply with the provisions of Section C402.5.3 for vertical *fenestration*.

**C402.6 Air leakage—building thermal envelope.** The *building thermal envelope* shall comply with Sections C402.6.1 through C402.6.7.

**C402.6.1 Air barriers.** A continuous *air barrier* shall be provided throughout the *building thermal envelope*. The *air barrier* is permitted to be located at any combination of inside, outside or within the *building thermal envelope*. The *air barrier* shall comply with Sections C402.6.1.1 and C402.6.1.2. The *air leakage* performance of the *air barrier* shall be verified in accordance with Section C402.6.2.

**Exception:** *Air barriers* are not required in buildings located in *Climate Zone* 2B.

**C402.6.1.1 Air barrier design and documentation requirements.** Design of the continuous *air barrier* shall be documented as follows:

1. Components comprising the continuous *air barrier* and their position within each *building thermal envelope* assembly shall be identified.
2. Joints, interconnections and penetrations of the continuous *air barrier* components shall be detailed.
3. The continuity of the *air barrier* building element assemblies that enclose *conditioned space* or provide a boundary between *conditioned space* and unconditioned space shall be identified.
4. Documentation of the continuous *air barrier* shall detail methods of sealing the *air barrier,* such as wrapping, caulk- ing, gasketing, taping or other *approved* methods at the following locations:
   1. Joints around *fenestration* and door frames.
   2. Joints between walls and floors; between walls at building corners; between walls and roofs, including para- pets and copings; where *above-grade walls* meet foundations; and at similar intersections.
   3. Penetrations or attachments through the continuous *air barrier*.
   4. Building assemblies used as *ducts* or plenums.
   5. Changes in continuous *air barrier* materials and assemblies.
5. Identify where testing will or will not be performed in accordance with Section C402.6.2. Where testing will not be performed, a plan for field inspections required by Section C402.6.2.3 shall be provided that includes the following:
   1. A schedule for periodic inspection.
   2. The continuous *air barrier* scope of work.
   3. A list of critical inspection items.
   4. Inspection documentation requirements.
   5. Provisions for corrective actions where needed.

**C402.6.1.2 Air barrier construction.** The *continuous air barrier* shall be constructed to comply with the following:

1. The *air barrier* shall be continuous for all assemblies that compromise the *building thermal envelope* and across the joints and assemblies.
2. *Air barrier* joints and seams shall be sealed, including sealing transitions in places and changes in materials. The joints and seals shall be securely installed in or on the joint for its entire length so as not to dislodge, loosen or other- wise impair its ability to resist positive and negative pressure differentials such as those from wind, stack effect and mechanical ventilation.
3. Penetrations of the *air barrier* shall be caulked, gasketed or otherwise sealed in a manner compatible with the construction materials and location. Sealing shall allow for expansion, contraction and mechanical vibration. Sealing materials shall be securely installed around the penetration so as not to dislodge, loosen or otherwise impair the penetrations’ ability to resist positive and negative pressure. Sealing of concealed fire sprinklers, where required, shall be in a manner that is recommended by the fire sprinkler manufacturer. Caulking or other adhesive sealants shall not be used to fill voids between fire sprinkler cover plates and walls or ceilings.
4. Recessed lighting fixtures shall comply with Section C402.6.1.2.1. Where similar objects are installed that penetrate the *air barrier*, provisions shall be made to maintain the integrity of the *air barrier*.
5. Electrical and communication boxes shall comply with Section C402.6.1.2.2.

**C402.6.1.2.1 Recessed lighting.** Recessed luminaires installed in the *building thermal envelope* shall be all of the following:

* 1. IC-rated.
  2. *Labeled* as having an *air leakage* rate of not greater than 2.0 cfm (0.944 L/s) when tested in accordance with ASTM E283 at a 1.57 psf (75 Pa) pressure differential.
  3. Sealed with a gasket or caulk between the housing and interior wall or ceiling covering.

**C402.6.1.2.2 Electrical and communication boxes.** Electrical and communication boxes that penetrate the *air barrier* of the *building thermal envelope*, and that do not comply with Section C402.6.1.2.2.1, shall be caulked, taped, gasketed or otherwise sealed to the *air barrier* element being penetrated. All openings on the concealed portion of the box shall be sealed. Where present, insulation shall rest against all concealed portions of the box.

**C402.6.1.2.2.1 Air-sealed boxes.** Where air-sealed boxes are installed, they shall be marked in accordance with NEMA OS 4. Air-sealed boxes shall be installed in accordance with the manufacturer’s instructions.

**C402.6.2 Air leakage compliance.** *Air leakage* of the *building thermal envelope* shall be tested by an *approved* third party in accordance with Section C402.6.2.1. The measured *air leakage* shall not be greater than 0.35 cubic feet per minute per square foot (1.8 L/s x m2) of the *building thermal envelope* area at a pressure differential of 0.3 inch water gauge (75 Pa) with the calculated *building thermal envelope* surface area being the sum of the above- and below-grade *building thermal envelope*.

Exceptions:

1. Where the measured *air leakage* rate is greater than 0.35 cfm/ft2 (1.8 L/s × m2) but is not greater than 0.45 cfm/ft2 (2.3 L/s × m2), the *approved* third party shall perform a diagnostic evaluation using a smoke tracer or infrared imaging. The evaluation shall be conducted while the building is pressurized or depressurized along with a visual inspection of the *air barrier* in accordance with ASTM E1186. All identified leaks shall be sealed where such sealing can be made with- out damaging existing building components. A report specifying the corrective actions taken to seal leaks shall be deemed to establish compliance with the requirements of this section where submitted to the *code official* and the *building* owner. Where the measured *air leakage* rate is greater than 0.45 cfm/ft2 (2.3 L/s × m2), corrective actions must be made to the *building* and an additional test completed for which the results are 0.45 cfm/ft2 (2.3 L/s × m2) or less.
2. Buildings in Climate Zone 2B.
3. Buildings larger than 25,000 square feet (2323 m2) floor area in Climate Zones 0 through 4, other than Group I and R occupancies, that comply with Section C402.6.2.3.
4. As an alternative, *buildings* or portions of *buildings* containing Group I-1 and R-2 occupancies shall be permitted to be tested by an *approved* third party in accordance with Section C402.6.2.2. The reported *air leakage* of the *building ther- mal envelope* shall not be greater than 0.27 cfm/ft2 (1.4 L/s × m2) of the *testing unit enclosure area* at a pressure differential of 0.2 inch water gauge (50 Pa).

**C402.6.2.1 Whole building test method and reporting.** The *building thermal envelope* shall be tested by an *approved* third party in accordance with ASTM E3158 or an equivalent *approved* method. A report that includes the tested surface area, floor area, air by volume, stories above grade, and *air leakage* rates shall be submitted to the *code official* and the building *owner*.

Exceptions:

* 1. For *buildings* less than 10,000 square feet (929 m2), the entire *building thermal envelope* shall be permitted to be tested in accordance with ASTM E779, ASTM E3158, ASTM E1827 or an equivalent *approved* method.
  2. For *buildings* greater than 50,000 square feet (4645 m2), portions of the *building* shall be permitted to be tested and the measured *air leakage* shall be area weighted by the surface areas of the *building thermal envelope* in each portion. The weighted-average tested *air leakage* shall not be greater than the whole building *air leakage* limit. The following portions of the *building* shall be tested:
     1. The entire *building thermal envelope* area of stories that have any *conditioned spaces* directly under a roof.
     2. The entire *building thermal envelope* area of stories that have a *building entrance*, have a floor over unconditioned space, have a loading dock or that are below grade.
     3. Representative above-grade portions of the building totaling not less than 25 percent of the wall area enclosing the remaining *conditioned space*.

**C402.6.2.2 Dwelling and sleeping unit enclosure method and reporting.** The *building thermal envelope* shall be tested for *air leakage* in accordance with ASTM E779, ANSI/RESNET/ICC 380, ASTM E1827 or an equivalent *approved* method. Where multiple *dwelling units* or *sleeping units* or other spaces are contained within one *building thermal envelope*, each shall be considered an individual testing unit, and the *building air leakage* shall be the weighted average of all tested unit results, weighted by each *testing unit enclosure area*. Units shall be tested without simultaneously testing adjacent units and shall be separately tested as follows:

1. Where buildings have less than eight total dwelling or *sleeping units*, each testing unit shall be tested.
2. Where buildings have eight or more dwelling or *sleeping units*, the greater of seven units or 20 percent of the units in the building shall be tested, including a top floor unit, a middle floor unit, a ground floor unit and a unit with the larg- est *testing unit enclosure area*. For each tested unit that exceeds the maximum *air leakage* rate, an additional three units shall be tested, including a mixture of testing unit types and locations.
3. *Enclosed spaces* with not less than one *exterior wall* in the *building thermal envelope* shall be tested in accordance with Section C402.6.2.1.

**Exception:** Corridors, stairwells, and *enclosed spaces* having a *conditioned floor area* not greater than 1,500 square feet (139 m2) shall be permitted to comply with Section C402.6.2.3 and either Section C402.6.2.3.1 or Section C402.6.2.3.2.

**C402.6.2.3 Building thermal envelope design and construction verification criteria.** Where Section C402.6.2.1 and C402.6.2.2 are not applicable the installation of the continuous *air barrier* shall be verified by the *code official*, a *registered design professional* or *approved* agency in accordance with the following:

1. A review of the *construction documents* and other supporting data shall be conducted to assess compliance with the requirements in Section C402.6.1.
2. Inspection of continuous *air barrier* components and assemblies shall be conducted during construction to verify compliance with the requirements of Sections C402.6.2.3.1 and C402.6.2.3.2. The *air barrier* shall be provided with access for inspection and repair.
3. A final inspection report shall be provided for inspections completed by the *registered design professional* or *approved* agency. The inspection report shall be provided to the *building owner* or *owner’s* authorized agent and the *code official*. The report shall identify deficiencies found during inspection and details of corrective measures taken.

**C402.6.2.3.1 Materials.** Materials with an air permeability not greater than 0.004 cfm/ft2(0.02 L/s × m 2) under a pressure differential of 0.3 inch water gauge (75 Pa) when tested in accordance with ASTM E2178 shall comply with this section. Mate- rials in Items 1 through 16 shall be deemed to comply with this section, provided that joints are sealed and materials are installed as *air barriers* in accordance with the manufacturer’s instructions.

* 1. Plywood with a thickness of not less than 3/8 inch (10 mm).
  2. Oriented strand board having a thickness of not less than 3/8 inch (10 mm).
  3. Extruded polystyrene insulation board having a thickness of not less than 1/2 inch (12.7 mm).
  4. Foil-back polyisocyanurate insulation board having a thickness of not less than 1/2 inch (12.7 mm).
  5. Closed-cell spray foam having a minimum density of 1.5 pcf (2.4 kg/m3) and having a thickness of not less than 11/2 inches (38 mm).
  6. Open-cell spray foam with a density between 0.4 and 1.5 pcf (0.6 and 2.4 kg/m3) and having a thickness of not less than 4.5 inches (113 mm).
  7. Exterior or interior gypsum board having a thickness of not less than 1/2 inch (12.7 mm).
  8. Cement board having a thickness of not less than 1/2 inch (12.7 mm).
  9. Built-up roofing membrane.
  10. Modified bituminous roof membrane.
  11. Single-ply roof membrane.
  12. A Portland cement/sand parge, or gypsum plaster having a thickness of not less than 5/8 inch (15.9 mm).
  13. Cast-in-place and precast concrete.
  14. Fully grouted concrete block masonry.
  15. Sheet steel or aluminum.
  16. Solid or hollow masonry constructed of clay or shale masonry units.

**C402.6.2.3.2 Assemblies.** Assemblies of materials and components with an average *air leakage* not greater than 0.04 cfm/ft2 (0.2 L/s × m2) under a pressure differential of 0.3 inch of water gauge (75 Pa) where tested in accordance with ASTM E2357,ASTM E1677, ASTM D8052 or ASTM E283 shall comply with this section. Assemblies listed in Items 1 through 3 below shall be deemed to comply, provided that joints are sealed and the requirements of Section C402.6.1.2 are met.

1. Concrete masonry walls coated with either one application of block filler or two applications of a paint or sealer coating.
2. Masonry walls constructed of clay or shale masonry units with a nominal width greater than or equal to 4 inches (102 mm).
3. A Portland cement/sand parge, stucco or plaster not less than 1/2 inch (12.7 mm) in thickness.

**C402.6.3 Air leakage of fenestration and opaque doors.** The *air leakage* of *fenestration* and opaque door assemblies shall comply with Table C402.6.3. Testing shall be conducted by an accredited, independent testing laboratory in accordance with applicable reference test standards in Table C402.6.3 and *labeled* by the manufacturer.

Exceptions:

1. Field-fabricated *fenestration* assemblies that are sealed in accordance with Section C402.6.1.
2. *Fenestration* in *buildings* that is tested in accordance with Section C402.6.2 is not required to meet the *air leakage*

requirements in Table C402.6.3.

|  |  |  |
| --- | --- | --- |
| **TABLE C402.6.3—MAXIMUM AIR LEAKAGE RATE FOR FENESTRATION ASSEMBLIES** | | |
| **FENESTRATION ASSEMBLY** | **MAXIMUM RATE (cfm/ft2)** | **TEST PROCEDURE** |
| Windows | 0.20a | AAMA/WDMA/CSA101/I.S.2/A440 or NFRC 400 |
| Sliding doors | 0.20a |
| Swinging doors | 0.20a |
| Skylights—with condensation weepage openings | 0.30 |
| Skylights—all other | 0.20a |
| Curtain walls | 0.06 | NFRC 400 or ASTM E283 at 1.57 psf (75 Pa) |
| Storefront glazing | 0.06 |
| Commercial glazed swinging entrance doors | 1.00 |
| Power-operated sliding doors and power operated folding doors | 1.00 |
| Revolving doors | 1.00 |
| Garage doors | 0.40 | ANSI/DASMA 105, NFRC 400, or ASTM E283 at 1.57 psf (75 Pa) |
| Rolling doors | 1.00 |
| High-speed doors | 1.30 |
| For SI: 1 cubic foot per minute = 0.47 L/s, 1 square foot = 0.093 m2.  a. The maximum rate for windows, sliding and swinging doors, and skylights is permitted to be 0.3 cfm per square foot of fenestration or door area when tested in accordance with AAMA/WDMA/CSA101/I.S.2/A440 at 6.24 psf (300 Pa). | | |

**C402.6.4 Doors and access openings to shafts, chutes, stairways and elevator lobbies.** Doors and *access* openings from *conditioned space* to shafts, chutes, stairways and elevator lobbies not within the scope of the *fenestration* assemblies covered by Section C402.6.3 shall be gasketed, weather-stripped or sealed.

Exceptions:

1. Door openings required to comply with Section 716 of the *International Building Code*.
2. Doors and door openings required by the *International Building Code* to comply with UL 1784.

**C402.6.5 Air intakes, exhaust openings, stairways and shafts.** Stairway enclosures, elevator shaft vents and other outdoor air intakes and exhaust openings integral to the *building thermal envelope* shall be provided with dampers in accordance with Section C403.7.7.

**C402.6.6 Vestibules.** *Building entrances* shall be protected with an enclosed vestibule. Doors opening into and out of the vesti- bule equipped with self-closing devices. Vestibules shall be designed so that in passing through the vestibule it is not necessary for the interior and exterior doors to open at the same time. The installation of one or more revolving doors in the *building entrance* shall not eliminate the requirement that a vestibule be provided on any doors adjacent to revolving doors.

**Exceptions:** Vestibules are not required for the following:

1. Buildings in Climate Zones 0 through 2.
2. Doors not intended to be used by the public, such as doors to mechanical or electrical *equipment rooms*, or intended solely for employee use.
3. Doors opening directly from a *sleeping unit* or *dwelling unit*.
4. Doors that open directly from a space less than 3,000 square feet (298 m2) in area.
5. Revolving doors.
6. Doors used primarily to facilitate vehicular movement or material handling and adjacent personnel doors.
7. Doors that have an air curtain unit with a velocity of not less than 6.56 feet per second (2 m/s) at 6 inches (152 mm) above the floor that has been tested in accordance with ANSI/AMCA 220 or ISO 27327-1 and installed in accordance with the manufacturer’s instructions. *Manual* or *automatic* controls shall be provided that will operate the *air curtain unit* with the opening and closing of the door and comply with Section C403.4.1.5. *Air curtain units* and their controls shall comply with Section C408.2.3.

**C402.6.7 Loading dock weather seals.** Cargo door openings and loading door openings shall be equipped with weather seals that restrict *air leakage* and provide direct contact along the top and sides of vehicles that are parked in the doorway.

**C402.7 Thermal bridges in above-grade walls.** *Thermal bridges* in *above-grade walls* shall comply with this section or an *approved* design.

Exceptions:

* 1. *Buildings* and structures located in Climate Zones 0 through 3.
  2. Any *thermal bridge* with a material thermal conductivity not greater than 3.0 Btu/h × ft × °F (5.19 W/m × K).
  3. Blocking, coping, flashing and other similar materials for attachment of roof coverings.
  4. *Thermal bridges* accounted for in the *U-factor* or *C-factor* for a *building thermal envelope*.

**C402.7.1 Balconies and floor decks.** Balconies and concrete floor decks shall not penetrate the *building thermal envelope*. Such assemblies shall be separately supported or shall be supported by structural attachments or elements that minimize thermal bridging through the *building thermal envelope*.

**Exceptions:** Balconies and concrete floor decks shall be permitted to penetrate the *building thermal envelope* where one of the following applies:

* + 1. An area-weighted *U-factor* is used for *above-grade wall* compliance that includes a *U-factor* of 0.8 Btu/h × °F × ft2 (1.38 W/m × K) for the area of the *above-grade wall* penetrated by the concrete floor deck in accordance with Section C402.1.2.1.5.
    2. An *approved* thermal break device with not less than R-10 insulation material is installed in accordance with the manufacturer’s instructions.
    3. An *approved* design where the *above-grade wall U-factor* used for compliance accounts for all balcony and concrete floor deck *thermal bridges*.

**C402.7.2 Cladding supports.** Linear elements supporting opaque cladding shall be offset from the structure with attachments that allow the *continuous insulation*, where present, to pass behind the cladding support element except at the point of attachment.

Exceptions:

1. An *approved* design where the *above-grade wall U-factor* used for compliance accounts for the cladding support element *thermal bridge*.
2. Anchoring for *curtain wall* and window wall systems where *curtain wall* and window wall systems comply with Section C402.7.4.

**C402.7.3 Structural beams and columns.** Structural steel and concrete beams and columns that project through the *building thermal envelope* shall be covered with not less than R-5 insulation for not less than 2 feet (610 mm) beyond the interior or exterior surface of an insulation component within the *building thermal envelope*.

Exceptions:

1. Where an *approved* thermal break device is installed in accordance with the manufacturer’s instructions.
2. An *approved* design where the *above-grade wall U-factor* used to demonstrate compliance accounts for the beam or column *thermal bridge*.

**C402.7.4 Vertical fenestration.** Vertical *fenestration* intersections with *above-grade walls* shall comply with one or more of the following:

1. Where *above-grade walls* include *continuous insulation*, the plane of the exterior glazing layer or, for metal frame *fenes- tration*, a nonmetal thermal break in the frame shall be positioned within 2 inches (610 mm) of the interior or exterior surface of the *continuous insulation*.
2. Where *above-grade walls* do not include *continuous insulation*, the plane of the exterior glazing layer or, for metal frame *fenestration*, a nonmetal thermal break in the frame shall be positioned within the thickness of the integral or *cavity insulation*.
3. The surface of the rough opening, not covered by the *fenestration* frame, shall be insulated with insulation of not less than R-3 material or covered with a wood buck that is not less than 1.5 inches (38 mm) thick.
4. For the intersection between vertical *fenestration* and opaque spandrel in a shared framing system, manufacturer’s data for the spandrel *U-factor* shall account for *thermal bridges*.

Exceptions:

* 1. Where an *approved* design for the *above-grade wall U-factor* used for compliance accounts for *thermal bridges* at the intersection with the vertical *fenestration*.
  2. Doors.

**C402.7.5 Parapets.** Parapets shall comply with one or more of the following as applicable:

1. Where *continuous insulation* is installed on the exterior side of the *above-grade wall* and the roof is insulated with insula- tion entirely above deck, the *continuous insulation* shall extend up both sides of the parapet not less than 2 feet (610 mm) above the roof covering or to the top of the parapet, whichever is less. Parapets that are an integral part of a fire-resis- tance rated wall, and the exterior continuous insulation applied to the parapet, shall comply with the fire-resistance ratings of the *International Building Code*.
2. Where *continuous insulation* is installed on the exterior side of the *above-grade wall* and the roof insulation is below the roof deck, the *continuous insulation* shall extend up the exterior side of the parapet to not less than the height of the top surface of the *roof assembly*.
3. Where *continuous insulation* is not installed on the exterior side of the *above-grade wall* and the roof is insulated with insulation entirely above deck, the wall cavity or integral insulation shall extend into the parapet up to the exterior face of the roof insulation or equivalent *R*-*value* insulation shall be installed not less than 2 feet (610 mm) horizontally inward on the underside of the roof deck.
4. Where *continuous insulation* is not installed on the exterior side of the *above-grade wall* and the roof insulation is below the roof deck, the wall and roof insulation components shall be adjacent to each other at the roof-ceiling-wall intersection.
5. Where a thermal break device with not less than R-10 insulation material aligned with the *above-grade wall* and roof insulation is installed in accordance with the manufacturer’s instructions.

**Exception:** An *approved design* where the *above-grade wall U-factor* used for compliance accounts for the parapet *thermal bridge*.

SECTION C403—BUILDING MECHANICAL SYSTEMS

**C403.1 General.** Mechanical systems and equipment serving the building heating, cooling, ventilating or refrig- erating needs shall comply with one of the following:

1. Section C403.1.1 and Sections C403.2 through C403.17.
2. *Data Centers* shall comply with Section C403.1.1, Section C403.1.2 and Sections C403.6 through C403.17.
3. Section C409.

**C403.1.1 Calculation of heating and cooling loads.** Design loads associated with heating, ventilating and air conditioning of the *building* shall be determined in accordance with ANSI/ASHRAE/ACCA Standard 183 or by an *approved* equivalent computational procedure using the design parameters specified in Chapter 3. Heat- ing and cooling loads shall be adjusted to account for load reductions that are achieved where energy recovery systems are utilized in the HVAC system in accordance with the ASHRAE HVAC Systems and Equip- ment Handbook by an *approved* equivalent computational procedure.

**C403.1.2 Data centers.** *Data center systems* shall comply with Sections 6 and 8 of ASHRAE 90.4.

**C403.2 System design.** Mechanical systems shall be designed to comply with Sections C403.2.1 through C403.2.3. Where elements of a building’s mechanical systems are addressed in Sections C403.3 through C403.14, such elements shall comply with the applica- ble provisions of those sections.

**C403.2.1 Zone isolation required.** HVAC systems serving *zones* that are over 25,000 square feet (2323 m2) in floor area or that span more than one floor and are designed to operate or be occupied nonsimultaneously shall be divided into isolation areas. Each isolation area shall be equipped with *isolation devices* and controls configured to automatically shut off the supply of condi- tioned air and outdoor air to and exhaust air from the isolation area. Each isolation area shall be controlled independently by a device meeting the requirements of Section C403.4.2.2. Central systems and plants shall be provided with controls and devices that will allow system and equipment operation for any length of time while serving only the smallest isolation area served by the system or plant.

Exceptions:

1. Exhaust air and outdoor air connections to isolation areas where the *fan system* to which they connect is not greater than 5,000 cfm (2360 L/s).
2. Exhaust airflow from a single isolation area of less than 10 percent of the design airflow of the exhaust system to which it connects.
3. Isolation areas intended to operate continuously or intended to be inoperative only when all other isolation areas in a

*zone* are inoperative.

**C403.2.2 Ventilation.** *Ventilation*, either natural or mechanical, shall be provided in accordance with Chapter 4 of the *Interna- tional Mechanical Code*. Where mechanical ventilation is provided, the system shall provide the capability to reduce the outdoor air supply to the minimum required by Chapter 4 of the *International Mechanical Code*.

**C403.2.3 Fault detection and diagnostics.** Buildings with a gross *conditioned floor area* of not less than 100,000 square feet (9290 m2) served by one or more HVAC systems that are controlled by a *direct digital control* (DDC) system shall include a fault detection and diagnostics (FDD) system to monitor the HVAC system’s performance and automatically identify faults. The *FDD system* shall:

1. Include permanently installed sensors and devices to monitor HVAC system performance.
2. Sample HVAC system performance at least once every 15 minutes.
3. Automatically identify and report HVAC system faults.
4. Automatically notify authorized personnel of identified HVAC system faults.
5. Automatically provide prioritized recommendations for *repair* of identified faults based on analysis of data collected from the sampling of HVAC system performance.
6. Be capable of transmitting the prioritized fault repair recommendations to remotely located authorized personnel.

**Exception:** R-1 and R-2 occupancies.

**C403.3 Heating and cooling equipment efficiencies.** Heating and cooling equipment installed in mechanical systems shall be sized in accordance with Section C403.3.1 and shall be not less efficient in the use of energy than as specified in Section C403.3.2.

**C403.3.1 Equipment sizing.** The output capacity of heating and cooling equipment shall be not greater than that of the smallest available equipment size that exceeds the loads calculated in accordance with Section C403.1.1. A single piece of equipment providing both heating and cooling shall satisfy this provision for one function with the capacity for the other function as small as possible, within available equipment options.

Exceptions:

* 1. Required standby equipment and systems provided with controls and devices that allow such systems or equipment to operate automatically only when the primary equipment is not operating.
  2. Multiple units of the same equipment type with combined capacities exceeding the design load and provided with controls that are configured to sequence the operation of each unit based on load.

**C403.3.2 HVAC equipment performance requirements.** Equipment shall meet the minimum efficiency requirements of Tables C403.3.2(1) through C403.3.2(16) when tested and rated in accordance with the applicable test procedure. Plate-type liquid-to- liquid heat exchangers shall meet the minimum requirements of AHRI 400. The efficiency shall be verified through certification under an *approved* certification program or, where a certification program does not exist, the equipment efficiency ratings shall be supported by data furnished by the manufacturer. Where multiple rating conditions or performance requirements are provided, the equipment shall satisfy all stated requirements. Where components, such as indoor or outdoor coils, from different manufacturers are used, calculations and supporting data shall be furnished by the designer that demonstrates that the combined efficiency of the specified components meets the requirements herein.

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| **TABLE C403.3.2(1)—ELECTRICALLY OPERATED UNITARY**  **AIR CONDITIONERS AND CONDENSING UNITS—MINIMUM EFFICIENCY REQUIREMENTSc** | | | | | |
| **EQUIPMENT TYPE** | **SIZE CATEGORY** | **HEADING SECTION TYPE** | **SUBCATEGORY OR RATING CONDITION** | **MINIMUM EFFICIENCY** | **TEST PROCEDUREa** |
| Air conditioners, air cooled | < 65,000 Btu/hb | All | Split system, three phase and applications outside US single phaseb | 13.4 SEER2 | AHRI 210/240—2023 |
| Single-package, three phase and applications outside US single phaseb | 13.4 SEER2 |
| Space constrained, air cooled | ≤ 30,000 Btu/hb | All | Split system, three phase and applications outside US single phaseb | 11.7 SEER2 | AHRI 210/240—2023 |
| Single package, three phase and applications outside US single phaseb | 11.7 SEER2 |
| Small duct, high velocity, air cooled | < 65,000 Btu/hb | All | Split system, three phase and applications outside US single phaseb | 12. 0 SEER2 | AHRI 210/240—2023 |
| Air conditioners, air cooled | ≥ 65,000 Btu/h and  < 135,000 Btu/h | Electric resistance (or none) | Split system and single package | 14.8 IEER | AHRI 340/360 |
| All other | 14.6 IEER |
| ≥ 135,000 Btu/h and  < 240,000 Btu/h | Electric resistance (or none) | 14.2 IEER |
| All other | 14.0 IEER |
| ≥ 240,000 Btu/h and  < 760,000 Btu/h | Electric resistance (or none) | Split system and single package | 13.2 IEER | AHRI 340/360 |
| All other | 13.0 IEER |
| ≥ 760,000 Btu/h | Electric resistance (or none) | 12.5 IEER |
| All other | 12.3 IEER |

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| **TABLE C403.3.2(1)—ELECTRICALLY OPERATED UNITARY**  **AIR CONDITIONERS AND CONDENSING UNITS—MINIMUM EFFICIENCY REQUIREMENTSc—continued** | | | | | |
| **EQUIPMENT TYPE** | **SIZE CATEGORY** | **HEADING SECTION TYPE** | **SUBCATEGORY OR RATING CONDITION** | **MINIMUM EFFICIENCY** | **TEST PROCEDUREa** |
| Air conditioners, water cooled | < 65,000 Btu/h | All | Split system and single package | 12.1 EER  12.3 IEER | AHRI 210/240 |
| ≥ 65,000 Btu/h and  < 135,000 Btu/h | Electric resistance (or none) | 12.1 EER  13.9 IEER | AHRI 340/360 |
| All other | 11.9 EER  13.7 IEER |
| ≥ 135,000 Btu/h and  < 240,000 Btu/h | Electric resistance (or none) | 12.5 EER  13.9 IEER |
| All other | 12.3 EER  13.7 IEER |
| ≥ 240,000 Btu/h and  < 760,000 Btu/h | Electric resistance (or none) | 12.4 EER  13.6 IEER |
| All other | 12.2 EER  13.4 IEER |
| ≥ 760,000 Btu/h | Electric resistance (or none) | 12.2 EER  13.5 IEER |
| All other | 12.0 EER  13.3 IEER |
| Air conditioners, evaporatively cooled | < 65,000 Btu/hb | All | Split systemand single package | 12.1 EER  12.3 IEER | AHRI 210/240 |
| ≥ 65,000 Btu/h and  < 135,000 Btu/h | Electric resistance (or none) | 12.1 EER  12.3 IEER | AHRI 340/360 |
| All other | 11.9 EER  12.1 IEER |
| ≥ 135,000 Btu/h and  < 240,000 Btu/h | Electric resistance (or none) | 12.0 EER  12.2 IEER |
| All other | 11.8 EER  12.0 IEER |
| ≥ 240,000 Btu/h and  < 760,000 Btu/h | Electric resistance (or none) | 11.9 EER  12.1 IEER |
| All other | 11.7 EER  11.9 IEER |
| ≥ 760,000 Btu/h | Electric resistance (or none) | 11.7 EER  11.9 IEER |
| All other | 11.5 EER  11.7 IEER |
| Condensing units, air cooled | ≥ 135,000 Btu/h | — | — | 10.5 EER  11.8 IEER | AHRI 365 |
| Condensing units, water cooled | ≥ 135,000 Btu/h | — | — | 13.5 EER  14.0 IEER | AHRI 365 |
| Condensing units, evaporatively cooled | ≥ 135,000 Btu/h | — | — | 13.5 EER  14.0 IEER | AHRI 365 |
| For SI: 1 British thermal unit per hour = 0.2931 W.   1. Chapter 6 contains a complete specification of the referenced standards, which include test procedures, including the reference year version of the test procedure. 2. Single-phase, US air-cooled air conditioners less than 65,000 Btu/h are regulated as consumer products by the US Department of Energy Code of Federal Regulations DOE 10 CFR 430. SEER and SEER2 values for single-phase products are set by the US Department of Energy. 3. DOE 10 CFR 430 Subpart B Appendix M1 includes the test procedure updates effective January 1, 2023, documented in AHRI 210/240—2023. | | | | | |

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| **TABLE C403.3.2(2)—ELECTRICALLY OPERATED AIR-COOLED UNITARY HEAT PUMPS—MINIMUM EFFICIENCY REQUIREMENTSc** | | | | | |
| **EQUIPMENT TYPE** | **SIZE CATEGORY** | **HEADING SECTION TYPE** | **SUBCATEGORY OR RATING CONDITION** | **MINIMUM EFFICIENCY** | **TEST PROCEDUREa** |
| Air cooled (cooling mode) | < 65,000 Btu/h | All | Split system, three phase and applications outside US single phaseb | 14.3 SEER2 | AHRI 210/240—2023 |
| Single package, three phase and applications outside US single phaseb | 13.4 SEER2 |
| Space constrained, air cooled (cooling mode) | ≤ 30,000 Btu/h | All | Split system, three phase and applications outside US single phaseb | 11.7 SEER2 | AHRI 210/240—2023 |
| Single package, three phase and applications outside US single phaseb | 11.7 SEER2 |
| Small duct, high velocity, air cooled (cooling mode) | < 65,000 Btu/h | All | Split system, three phase and applications outside US single phaseb | 12.0 SEER2 | AHRI 210/240—2023 |
| Air cooled (cooling mode) | ≥ 65,000 Btu/h and  < 135,000 Btu/h | Electric resistance (or none) | Split system and single package | 14.1 IEER | AHRI 340/360 |
| All other | 13.9 IEER |
| ≥ 135,000 Btu/h and  < 240,000 Btu/h | Electric resistance (or none) | 13.5 IEER |
| All other | 13.3 IEER |
| ≥ 240,000 Btu/h | Electric resistance (or none) | 12.5 IEER |
| All other | 12.3 IEER |
| Air cooled (heating mode) | < 65,000 Btu/h (cooling capacity) | — | Split system, three phase and applications outside US single phaseb | 7.5 HSPF2 | AHRI 210/240—2023 |
| Single package, three phase and applications outside US single phaseb | 6.7 HSPF2 |
| Space constrained, air cooled (heating mode) | ≤ 30,000 Btu/h (cooling capacity) | — | Split system, three phase and applications outside US single phaseb | 6.3 HSPF2 | AHRI 210/240—2023 |
| Single package, three phase and applications outside US single phaseb | 6.3 HSPF2 |
| Small duct high velocity, air cooled (heating mode) | < 65,000 Btu/h | — | Split system, three phase and applications outside US single phaseb | 6.1 HSPF2 | AHRI 210/240—2023 |
| Air cooled (heating mode) | ≥ 65,000 Btu/h and  < 135,000 Btu/h (cooling capacity) | — | 47°F db/43°F wb outdoor air | 3.40 COPH | AHRI 340/360 |
| 17°F db/15°F wb outdoor air | 2.25 COPH |
| ≥ 135,000 Btu/h and  < 240,000 Btu/h (cooling capacity) | 47°F db/43°F wb outdoor air | 3.30 SOPH |
| 17°F db/15°F wb outdoor air | 2.05 COPH |
| ≥ 240,000 Btu/h (cooling capacity) | 47°F db/43°F wb outdoor air | 3.20 COPH |
| 17°F db/15°F wb outdoor air | 2.05 COPH |
| For SI: 1 British thermal unit per hour = 0.2931 W, °C = (°F – 32)/1.8, wb = wet bulb, db = dry bulb.   1. Chapter 6 contains a complete specification of the referenced standards, which include test procedures, including the reference year version of the test procedure. 2. Single-phase, US air-cooled heat pumps less than 65,000 Btu/h are regulated as consumer products by the US Department of Energy Code of Federal Regulations DOE 10 CFR   430. SEER, SEER2 and HSPF values for single-phase products are set by the US Department of Energy.   1. DOE 10 CFR 430 Subpart B Appendix M1 includes the test procedure updates effective January 1, 2023, documented in AHRI 210/240—2023. | | | | | |

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| **TABLE C403.3.2(3)—LIQUID-CHILLING PACKAGES—MINIMUM EFFICIENCY REQUIREMENTSa, b, e** | | | | | |
| **EQUIPMENT TYPE** | **SIZE CATEGORY** | **UNITS** | **PATH A** | **PATH B** | **TEST PROCEDUREc** |
| Air cooled | < 150 tons | EER (Btu/Wh) | ≥ 10.100 FL | ≥ 9.700 FL | AHRI 550/590 |
| ≥ 13.700 IPLV.IP | ≥ 15.800 IPLV.IP |
| ≥ 150 tons | ≥ 10.100 FL | ≥ 9.700FL |
| ≥ 14.000 IPLV.IP | ≥ 16.100 IPLV.IP |
| Air cooled without condenser, electri- cally operated | All capacities | EER (Btu/Wh) | Air-cooled without condenser must be rated with matching condensers and comply with air-cooled chiller efficiency requirements | | AHRI 550/590 |
| Liquid-cooled, electrically operated positive displacement | < 75 tons | kW/ton | ≤ 0.750 FL | ≤ 0.780 FL | AHRI 550/590 |
| ≤ 0.600 IPLV.IP | ≤ 0.500 IPLV.IP |
| ≥ 75 tons and  < 150 tons | ≤ 0.720 FL | ≤ 0.750 FL |
| ≤ 0.560 IPLV.IP | ≤ 0.490 IPLV.IP |
| ≥ 150 tons and  < 300 tons | ≤ 0.660 FL | ≤ 0.680 FL |
| ≤ 0.540 IPLV.IP | ≤ 0.440 IPLV.IP |
| ≥ 300 tons and  < 600 tons | ≤ 0.610 FL | ≤ 0.625 FL |
| ≤ 0.520 IPLV.IP | ≤ 0.410 IPLV.IP |
| ≥ 600 tons | ≤ 0.560 FL | ≤ 0.585 FL |
| ≤ 0.500 IPLV.IP | ≤ 0.380 IPLV.IP |
| Liquid-cooled, electrically operated centrifugal | < 150 tons | kW/ton | ≤ 0.610 FL | ≤ 0.695 FL | AHRI 550/590 |
| ≤ 0.550 IPLV.IP | ≤ 0.440 IPLV.IP |
| ≥150 tons and  <300 tons | ≤ 0.610 FL | ≤ 0.635 FL |
| ≤ 0.550 IPLV.IP | ≤ 0.400 IPLV.IP |
| ≥ 300 tons and  < 400 tons | ≤ 0.560 FL | ≤ 0.595 FL |
| ≤ 0.520 IPLV.IP | ≤ 0.390 IPLV.IP |
| ≥ 400 tons and  < 600 tons | ≤ 0.560 FL | ≤ 0.585 FL |
| ≤ 0.500 IPLV.IP | ≤ 0.380 IPLV.IP |
| ≥ 600 tons | ≤ 0.560 FL | ≤ 0.585 FL |
| ≤ 0.500 IPLV.IP | ≤ 0.380 IPLV.IP |
| Air cooled absorption, single effect | All capacities | COP (W/W) | ≥ 0.600 FL | NAd | AHRI 560 |
| Liquid-cooled absorption, single effect | All capacities | COP (W/W) | ≥ 0.700 FL | NAd | AHRI 560 |
| Absorption double effect, indirect fired | All capacities | COP (W/W) | ≥ 1.000 FL | NAd | AHRI 560 |
| ≥ 0.150 IPLV.IP |
| Absorption double effect, direct fired | All capacities | COP (W/W) | ≥ 1.000 FL | NAd | AHRI 560 |
| ≥ 1.000 IPLV |
| 1. Chapter 6 contains a complete specification of the referenced standards, which include test procedures, including the reference year version of the test procedure. 2. The requirements for centrifugal chillers shall be adjusted for nonstandard rating conditions per Section C403.3.2.1 and are applicable only for the range of conditions listed there. The requirements for air-cooled, water-cooled positive displacement and absorption chillers are at standard rating conditions defined in the reference test procedure. 3. Both the full-load and IPLV.IP requirements must be met or exceeded to comply with this standard. When there is a Path B, compliance can be with either Path A or Path B for any application. 4. NA means the requirements are not applicable for Path B, and only Path A can be used for compliance. 5. FL is the full-load performance requirements, and IPLV.IP is for the part-load performance requirements. | | | | | |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **TABLE C403.3.2(4)—ELECTRICALLY OPERATED PACKAGED TERMINAL AIR CONDITIONERS,**  **PACKAGED TERMINAL HEAT PUMPS, SINGLE-PACKAGE VERTICAL AIR CONDITIONERS, SINGLE-PACKAGE VERTICAL HEAT PUMPS, ROOM AIR CONDITIONERS AND ROOM AIR-CONDITIONER HEAT PUMPS—MINIMUM EFFICIENCY REQUIREMENTSe** | | | | |
| **EQUIPMENT TYPE** | **SIZE CATEGORY (INPUT)** | **SUBCATEGORY OR RATING CONDITION** | **MINIMUM EFFICIENCYd** | **TEST PROCEDUREa** |
| PTAC (cooling mode) standard size | < 7,000 Btu/h | 95°F db/75°F wb outdoor airc | 11.9 EER | AHRI 310/380 |
| ≥ 7,000 Btu/h and  ≤ 15,000 Btu/h | 14.0 – (0.300 × Cap/1,000) EERd |
| > 15,000 Btu/h | 9.5 EER |
| PTAC (cooling mode) nonstandard sizea | < 7,000 Btu/h | 95°F db/75°F wb outdoor airc | 9.4 EER | AHRI 310/380 |
| ≥ 7,000 Btu/h and  ≤ 15,000 Btu/h | 10.9 – (0.213 × Cap/1,000) EERd |
| > 15,000 Btu/h | 7.7 EER |
| PTHP (cooling mode) standard size | < 7,000 Btu/h | 95°F db/75°F wb outdoor airc | 11.9 EER | AHRI 310/380 |
| ≥ 7,000 Btu/h and  ≤ 15,000 Btu/h | 14.0 – (0.300 × Cap/1,000) EERd |
| > 15,000 Btu/h | 9.5 EER |
| PTHP (cooling mode) nonstandard sizeb | < 7,000 Btu/h | 95°F db/75°F wb outdoor airc | 9.3 EER | AHRI 310/380 |
| ≥ 7,000 Btu/h and  ≤ 15,000 Btu/h | 10.8 – (0.213 × Cap/1,000) EERd |
| > 15,000 Btu/h | 7.6 EER |
| PTHP (heating mode) standard size | < 7,000 Btu/h | 47°F db/43°F wb outdoor air | 3.3 COPH | AHRI 310/380 |
| ≥ 7,000 Btu/h and  ≤ 15,000 Btu/h | 3.7 – (0.052 × Cap/1,000) COP d  H |
| > 15,000 Btu/h | 2.90 COPH |
| PTHP (heating mode) nonstandard sizeb | < 7,000 Btu/h | 47°F db/43°F wb outdoor air | 2.7 COPH | AHRI 310/380 |
| ≥ 7,000 Btu/h and  ≤ 15,000 Btu/h | 2.9 – (0.026 × Cap/1000) COP d  H |
| > 15,000 Btu/h | 2.5 COPH |
| SPVAC (cooling mode) single and three phase | < 65,000 Btu/h | 95°F db/75°F wb outdoor airc | 11.0 EER | AHRI 390 |
| ≥ 65,000 Btu/h and  ≤ 135,000 Btu/h | 10.0 EER |
| ≥ 135,000 Btu/h and  ≤ 240,000 Btu/h | 10.0 EER |
| SPVHP (cooling mode) | < 65,000 Btu/h | 95°F db/75°F wb outdoor airc | 11.0 EER | AHRI 390 |
| ≥ 65,000 Btu/h and  ≤ 135,000 Btu/h | 10.0 EER |
| ≥ 135,000 Btu/h and  ≤ 240,000 Btu/h | 10. 0 EER |
| SPVHP (heating mode) | < 65,000 Btu/h | 47°F db/43°F wb outdoor air | 3.3 COPH | AHRI 390 |
| ≥ 65,000 Btu/h and  ≤ 135,000 Btu/h | 3.0 COPH |
| ≥ 135,000 Btu/h and  ≤ 240,000 Btu/h | 3.0 COPH |
| Room air conditioners without reverse cycle with louvered sides for appli- cations outside USd | < 6,000 Btu/h | — | 11.0 CEER | ANSI/AHAM RAC-1 |
| ≥ 6,000 Btu/h and  < 8,000 Btu/h | — | 11.0 CEER |
| ≥ 8,000 Btu/h and  < 14,000 Btu/h | — | 10.9 CEER |
| ≥ 14,000 Btu/h and  < 20,000 Btu/h | — | 10.7 CEER |
| ≥ 20,000 Btu/h and  < 28,000 Btu/h | — | 9.4 CEER |
| ≥ 28,000 Btu/h | — | 9.0 CEER |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **TABLE C403.3.2(4)—ELECTRICALLY OPERATED PACKAGED TERMINAL AIR CONDITIONERS,**  **PACKAGED TERMINAL HEAT PUMPS, SINGLE-PACKAGE VERTICAL AIR CONDITIONERS, SINGLE-PACKAGE VERTICAL HEAT PUMPS, ROOM AIR CONDITIONERS AND ROOM AIR-CONDITIONER HEAT PUMPS—MINIMUM EFFICIENCY REQUIREMENTSe—continued** | | | | |
| **EQUIPMENT TYPE** | **SIZE CATEGORY (INPUT)** | **SUBCATEGORY OR RATING CONDITION** | **MINIMUM EFFICIENCYd** | **TEST PROCEDUREa** |
| Room air conditioners without louvered sides | < 6,000 Btu/h | — | 10.0 CEER | ANSI/AHAM RAC-1 |
| ≥ 6,000 Btu/h and  < 8,000 Btu/h | — | 10.0 CEER |
| ≥ 8,000 Btu/h and  < 11,000 Btu/h | — | 9.6 CEER |
| ≥ 11,000 Btu/h and  < 14,000 Btu/h | — | 9.5 CEER |
| ≥ 14,000 Btu/h and  < 20,000 Btu/h | — | 9.3 CEER |
| ≥ 20,000 Btu/h | — | 9.4 CEER |
| Room air conditioners with reverse cycle, with louvered sides for appli- cations outside USd | < 20,000 Btu/h | — | 9.8 CEER | ANSI/AHAM RAC-1 |
| ≥ 20,000 Btu/h | — | 9.3 CEER |
| Room air conditioners with reverse cycle without louvered sides for appli- cations outside USd | < 14,000 Btu/h | — | 9.3 CEER | ANSI/AHAM RAC-1 |
| ≥ 14,000 Btu/h | — | 8.7 CEER |
| Room air conditioners, casement only for appli- cations outside USd | All | — | 9.5 CEER | ANSI/AHAM RAC-1 |
| Room air conditioners, casement slider for appli- cations outside USd | All | — | 10.4 CEER | ANSI/AHAM RAC-1 |
| For SI: 1 British thermal unit per hour = 0.2931 W, °C = (°F – 32)/1.8, wb = wet bulb, db = dry bulb.  “Cap” = The rated cooling capacity of the project in Btu/h. Where the unit’s capacity is less than 7,000 Btu/h, use 7,000 Btu/h in the calculation. Where the unit’s capacity is greater than 15,000 Btu/h, use 15,000 Btu/h in the calculations.   1. Chapter 6 contains a complete specification of the referenced standards, which include test procedures, including the reference year version of the test procedure. 2. Nonstandard size units must be factory labeled as follows: “MANUFACTURED FOR NONSTANDARD SIZE APPLICATIONS ONLY; NOT TO BE INSTALLED IN NEW STANDARD PROJECTS.” Nonstandard size efficiencies apply only to units being installed in existing sleeves having an external wall opening of less than 16 inches high or less than 42 inches wide and having a cross-sectional area less than 670 square inches. 3. The cooling-mode wet bulb temperature requirement only applies for units that reject condensate to the condenser coil. 4. Room air conditioners are regulated as consumer products by 10 CFR 430. For US applications of room air conditioners, refer to Informative Appendix F, Table F-3, for the US DOE minimum efficiency requirements for US applications. 5. “Cap” in EER and COPH equations for PTACs and PTHPs means cooling capacity in Btu/h at 95°F outdoor dry-bulb temperature. | | | | |

**COMMERCIAL ENERGY EFFICIENCY**

**2024 INTERNATIONAL ENERGY CONSERVATION CODE®**

**93**

|  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE C403.3.2(5)—WARM-AIR FURNACES AND COMBINATION WARM-AIR FURNACES/**  **AIR-CONDITIONING UNITS, WARM-AIR DUCT FURNACES AND UNIT HEATERS—MINIMUM EFFICIENCY REQUIREMENTSg** | | | | | | | | |
| **DESCRIPTION** | **FUEL** | **ELECTRIC POWER PHASE** | **APPLICATION LOCATION** | **HEATING CAPACITY**  **(INPUT), Btu/hb** | **COMBO-UNIT COOLING CAPACITY, Btu/h** | **SUBTYPE** | **MINIMUM EFFICIENCY** | **TEST PROCEDUREa** |
| Warm-air furnace | Gas | 1 | Inside US | < 225,000 | < 65,000 | See Informative Appendix F, Table F-4f | | |
| Warm-air furnace | Gas | 1 | Inside US | < 225,000 | ≥ 65,000 | Nonweatherized | 80% AFUE | Appendix Ng |
| Weatherized | 81% AFUE or 80% E c  t | Appendix Ng |
| ANSI Z21.47 |
| Warm-air furnace | Gas | 1 | Outside US | < 225,000 | All | Nonweatherized | 80% AFUE | Appendix Ng |
| Weatherized | 81% AFUE or 80% E c  t | Appendix Ng |
| ANSI Z21.47 |
| Warm-air furnace | Gas | 3 | All | < 225,000 | All | Nonweatherized | 80% AFUE | Appendix Ng |
| Weatherized | 81% AFUE or 80% E c  t | Appendix Ng |
| ANSI Z21.47 |
| Warm-air furnace | Gas | All | All | ≥ 225,000 and  ≤ 400,000 | All | All | 81% E c  t | ANSI Z21.47 |
| Warm-air furnace | Gas | All | Inside US | > 400,000 | All | All | 80%E c before 1/1/2023  t  81% E c after 1/1/2023  t | ANSI Z21.47 |
| Warm-air furnace | Gas | All | Outside US | > 400,000 | All | All | 80%Etc before 1/1/2023 81% Etc after 1/1/2023 | ANSI Z21.47 or ANSI Z83.8 |
| Warm-air furnace | Oil | 1 | Inside US | < 225,000 | < 65,000 | See Informative Appendix F, Table F-4f | | |
| Warm-air furnace | Oil | 1 | Inside US | < 225,000 | ≥ 65,000 | Nonweatherized | 83% AFUE | Appendix Ng |
| Weatherized | 78% AFUE or 80% E d  t | Appendix Ng |
| Section 42 UL 727 |
| Warm-air furnace | Oil | 1 | Outside US | < 225,000 | All | Nonweatherized | 83% AFUE | Appendix Ng |
| Weatherized | 78% AFUE or 80% E d  t | Appendix Ng |
| Section 42 UL 727 |
| Warm-air furnace | Oil | 3 | All | <225,000 | All | Nonweatherized | 83% AFUE | Appendix Ng |
| Weatherized | 78% AFUE or 80%E d  t | Appendix Ng |
| Section 42 UL 727 |
| Warm-air furnace | Oil | All | All | ≥ 225,000 | All | All | d  82% Et | Section 42 UL 727 |
| Warm-air furnace | Electric | 1 | Inside US | < 225,000 | < 65,000 | See Informative Appendix F, Table F-4f | | |
| Warm-air furnace | Electric | 1 | Inside US | < 225,000 | ≥ 65,000 | All | 96% AFUE | Appendix Ng |
| Warm-air furnace | Electric | 1 | Outside US | < 225,000 | All | All | 96% AFUE | Appendix Ng |
| Warm-air furnace | Electric | 3 | All | < 225,000 | All | All | 96% AFUE | Appendix Ng |
| Warm-air duct furnaces | Gas | All | All | All | All | All | 80% Ecd | ANSI Z83.8 |

|  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE C403.3.2(5)—WARM-AIR FURNACES AND COMBINATION WARM-AIR FURNACES/**  **AIR-CONDITIONING UNITS, WARM-AIR DUCT FURNACES AND UNIT HEATERS—MINIMUM EFFICIENCY REQUIREMENTSg—continued** | | | | | | | | |
| **DESCRIPTION** | **FUEL** | **ELECTRIC POWER PHASE** | **APPLICATION LOCATION** | **HEATING CAPACITY**  **(INPUT), Btu/hb** | **COMBO-UNIT COOLING CAPACITY, Btu/h** | **SUBTYPE** | **MINIMUM EFFICIENCY** | **TEST PROCEDUREa** |
| Warm-air unit heaters | Gas | All | All | All | All | All | 80% E d, e  c | ANSI Z83.8 |
| Warm-air unit heaters | Oil | All | All | All | All | All | 80% E d, e  c | Section 40 UL 731 |
| For SI: 1 British thermal unit per hour = 0.2931 W.   1. Chapter 6 contains a complete specification of the referenced standards, which include test procedures, including the reference year version of the test procedure. For this table, the following applies:    * Appendix N = 10 CFR 430 Appendix N    * ANSI Z21.47 = Section 2.39, Thermal Efficiency, ANSI Z21.47    * ANSI Z83.3 = Section 2.10, Efficiency, ANSI Z83.3    * UL 727 = Section 42, Combustion, UL 727    * UL 731 = Section 40, Combustion, UL 731 2. Compliance of multiple firing rate units shall be at the maximum firing rate. 3. *Et* = thermal efficiency. Units must also include an interrupted or intermittent ignition device (IID), have jacket losses not exceeding 0.75 percent of the input rating, and have either power venting or a flue damper. A vent damper is an acceptable alternative to a flue damper for those furnaces where combustion air is drawn from the conditioned space. 4. *Ec* = combustion efficiency (100 percent less flue losses). See test procedure for detailed discussion. 5. Units must also include an interrupted or intermittent ignition device (IID) and have either power venting or an *automatic* flue damper. 6. Includes combination units with cooling capacity < 65,000 Btu/h. For US applications of federally covered < 225,000 Btu/h products, see Informative Appendix F, Table F-4. 7. 10 CFR 430 is limited to-single phase equipment that is not contained within the same cabinet with a central air conditioner whose rated cooling capacity is above 65,000 Btu/h but for the test and rating procedures are not impacted for three-phase and can be used for AFUE ratings for ASHRAE/IES Standard 90.1 three-phase products and single-phase products with a cooling capacity greater than 65,000 Btu/h. | | | | | | | | |

**COMMERCIAL ENERGY EFFICIENCY**

**94**

**2024 INTERNATIONAL ENERGY CONSERVATION CODE®**

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **TABLE C403.3.2(6)—GAS- AND OIL-FIRED BOILERS—MINIMUM EFFICIENCY REQUIREMENTS** | | | | |
| **EQUIPMENT TYPEb** | **SUBCATEGORY OR RATING CONDITION** | **SIZE CATEGORY (INPUT)** | **MINIMUM EFFICIENCY** | **TEST PROCEDUREa** |
| Boilers, hot water | Gas fired | < 300,000 Btu/hg, h for applications outside US | 84% AFUE | DOE 10 CFR 430 Appendix N |
| ≥ 300,000 Btu/h and  ≤ 2,500,000 Btu/he | 84% *Et*d | DOE 10 CFR 431.86 |
| > 2,500,000 Btu/hb and  ≤ 10,000,000 Btu/hb | 82% *E* c  *c* |
| > 10,000,000 Btu/hb | 82% *E* c  *c* |
| Oil firedf | < 300,000 Btu/hg, h for applications outside US | 86% AFUE | DOE 10 CFR 430 Appendix N |
| ≥ 300,000 Btu/h and  ≤ 2,500,000 Btu/he | 82% *Et*d | DOE 10 CFR 431.86 |
| > 2,500,000 Btu/hb and  ≤ 10,000,000 Btu/hb | 84% *E* c  *c* |
| > 10,000,000 Btu/hb | c  84% *Ec* |
| Boilers, steam | Gas fired | < 300,000 Btu/hg for applications outside US | 82% AFUE | DOE 10 CFR 430 Appendix N |
| Gas fired—all, except natural draft | ≥ 300,000 Btu/h and  ≤ 2,500,000 Btu/he | 79% *Et*d | DOE 10 CFR 431.86 |
| > 2,500,000 Btu/hb and  ≤ 10,000,000 Btu/hb | 79% *Et*d |
| > 10,000,000 Btu/hb | 79% *Et*d |
| Gas fired—natural draft | ≥ 300,000 Btu/h and  ≤ 2,500,000 Btu/he | 79% *Et*d |
| > 2,500,000 Btu/hb | 79% *Et*d |
| Oil firedf | < 300,000 Btu/hg for applications outside US | 82% AFUE | DOE 10 CFR 430 Appendix N |
| ≥ 300,000 Btu/h and  ≤ 2,500,000 Btu/he | 84% *Et*d | DOE 10 CFR 431.86 |
| > 2,500,000 Btu/hb and  ≤ 10,000,000 Btu/hb | 81% *Et*d |
| > 10,000,000 Btu/hb | 81% *Et*d |
| For SI: 1 British thermal unit per hour = 0.2931 W.   1. Chapter 6 contains a complete specification of the referenced standards, which include test procedures, including the reference year version of the test procedure. 2. These requirements apply to boilers with rated input of 8,000,000 Btu/h or less that are not packaged boilers and to all packaged boilers. Minimum efficiency requirements for boilers cover all capacities of packaged boilers. 3. *Ec* = Combustion efficiency (100 percent less flue losses). 4. *Et* = Thermal efficiency. 5. Maximum capacity—minimum and maximum ratings as provided for and allowed by the unit’s controls. 6. Includes oil-fired (residual). 7. Boilers shall not be equipped with a constant burning pilot light. 8. A boiler not equipped with a tankless domestic water-heating coil shall be equipped with an automatic means for adjusting the temperature of the water such that an incre- mental change in inferred heat load produces a corresponding incremental change in the temperature of the water supplied. | | | | |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **TABLE C403.3.2(7)—PERFORMANCE REQUIREMENTS FOR HEAT REJECTION EQUIPMENT—MINIMUM EFFICIENCY REQUIREMENTS** | | | | |
| **EQUIPMENT TYPE** | **TOTAL SYSTEM HEAT- REJECTION CAPACITY AT RATED CONDITIONS** | **SUBCATEGORY OR RATING CONDITIONh** | **PERFORMANCE REQUIREDa, b, c, f, g** | **TEST PROCEDUREd, e** |
| Propeller or axial fan  open-circuit cooling towers | All | 95°F entering water 85°F leaving water 75°F entering wb | ≥ 40.2 gpm/hp | CTI ATC-105 and CTI STD-201 RS |
| Centrifugal fan open-circuit cooling towers | All | 95°F entering water 85°F leaving water 75°F entering wb | ≥ 20.0 gpm/hp | CTI ATC-105 and CTI STD-201 RS |
| Propeller or axial fan closed-circuit cooling towers | All | 102°F entering water 90°F leaving water 75°F entering wb | ≥ 16.1 gpm/hp | CTI ATC-105S and CTI STD-201 RS |
| Centrifugal fan closed- circuit cooling towers | All | 102°F entering water 90°F leaving water 75°F entering wb | ≥ 7.0 gpm/hp | CTI ATC-105S and CTI STD-201 RS |
| Propeller or axial fan dry coolers (air-cooled fluid coolers) | All | 115°F entering water 105°F leaving water 95°F entering wb | ≥ 4.5 gpm/hp | CTI ATC-105DS |
| Propeller or axial fan evaporative condensers | All | R-448A test fluid  165°F entering gas temperature 105°F condensing temperature 75°F entering wb | ≥ 160,000 Btu/h × hp | CTI ATC-106 |
| Propeller or axial fan evaporative condensers | All | Ammonia test fluid  140°F entering gas temperature  96.3°F condensing temperature 75°F entering wb | ≥ 134,000 Btu/h × hp | CTI ATC-106 |
| Centrifugal fan evaporative condensers | All | R-448A test fluid  165°F entering gas temperature 105°F condensing temperature 75°F entering wb | ≥ 137,000 Btu/h × hp | CTI ATC-106 |
| Centrifugal fan evaporative condensers | All | Ammonia test fluid  140°F entering gas temperature  96.3°F condensing temperature 75°F entering wb | ≥ 110,000 Btu/h × hp | CTI ATC-106 |
| Air-cooled condensers | All | 125°F condensing temperature 190°F entering gas temperature 15°F subcooling  95°F entering db | ≥ 176,000 Btu/h × hp | AHRI 460 |
| For SI: °C = (°F – 32)/1.8, L/s × kW = (gpm/hp)/(11.83), COP = (Btu/h × hp)/(2550.7), db = dry bulb temperature, wb = wet bulb temperature.   1. For purposes of this table, open-circuit cooling tower performance is defined as the water-flow rating of the tower at the thermal rating condition listed in the table divided by the fan motor nameplate power. 2. For purposes of this table, closed-circuit cooling tower performance is defined as the process water-flow rating of the tower at the thermal rating condition listed in the table divided by the sum of the fan motor nameplate power and the integral spray pump motor nameplate power. 3. For purposes of this table, dry-cooler performance is defined as the process water-flow rating of the unit at the thermal rating condition listed in the table divided by the total fan motor nameplate power of the unit, and air-cooled condenser performance is defined as the heat rejected from the refrigerant divided by the total fan motor nameplate power of the unit. 4. ASHRAE 90.1 Section 13 contains a complete specification of the referenced test procedure, including the referenced year version of the test procedure. 5. The efficiencies and test procedures for both open- and closed-circuit cooling towers are not applicable to hybrid cooling towers that contain a combination of separate wet and dry heat exchange sections. The certification requirements do not apply to field-erected cooling towers. 6. All cooling towers shall comply with the minimum efficiency listed in the table for that specific type of tower with the capacity effect of any project-specific accessories and/or options included in the capacity of the cooling tower. 7. For purposes of this table, evaporative condenser performance is defined as the heat rejected at the specified rating condition in the table, divided by the sum of the fan motor nameplate power and the integral spray pump nameplate power. 8. Requirements for evaporative condensers are listed with ammonia R-717 and R-448A as test fluids in the table. Evaporative condensers intended for use with halocarbon refrigerants other than R-448A must meet the minimum efficiency requirements listed with R-448A as the test fluid. For ammonia, the condensing temperature is defined as the saturation temperature corresponding to the refrigerant pressure at the condenser entrance. For R-448A, which is a zeotropic refrigerant, the condensing temperature is defined as the arithmetic average of the dew point and the bubble point temperatures corresponding to the refrigerant pressure at the condenser entrance. | | | | |

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| **TABLE C403.3.2(8)—ELECTRICALLY OPERATED**  **VARIABLE-REFRIGERANT-FLOW AIR CONDITIONERS—MINIMUM EFFICIENCY REQUIREMENTS** | | | | | |
| **EQUIPMENT TYPE** | **SIZE CATEGORY** | **HEATING SECTION TYPE** | **SUBCATEGORY OR RATING CONDITION** | **MINIMUM EFFICIENCY** | **TEST PROCEDUREa** |
| VRF air conditioners, air cooled | < 65,000 Btu/h three-phase for applications in the US and single- and three-phase for applications outside the US | All | VRF multisplit system | 13.0 SEER | AHRI 210/240 |
| ≥ 65,000 Btu/h and  < 135,000 Btu/h | Electric resistance (or none) | VRF multisplit system | 10.5 EER  15.5 IEER | AHRI 1230 |
| ≥ 135,000 Btu/h and  < 240,000 Btu/h | Electric resistance (or none) | VRF multisplit system | 10.3 EER  14.9 IEER |
| ≥ 240,000 Btu/h | Electric resistance (or none) | VRF multisplit system | 9.5 EER  13.9 IEER |
| For SI: 1 British thermal unit per hour = 0.2931 W.  a. Chapter 6 contains a complete specification of the referenced standards, which include test procedures, including the reference year version of the test procedure. | | | | | |

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| **TABLE C403.3.2(9)—ELECTRICALLY OPERATED**  **VARIABLE-REFRIGERANT-FLOW AND APPLIED HEAT PUMPS—MINIMUM EFFICIENCY REQUIREMENTS** | | | | | |
| **EQUIPMENT TYPE** | **SIZE CATEGORY** | **HEATING SECTION TYPE** | **SUBCATEGORY OR RATING CONDITION** | **MINIMUM EFFICIENCY** | **TEST PROCEDUREa** |
|  | < 65,000 Btu/h three-phase for |  |  |  |  |
|  | applications in the US and single- and three- phase for applications outside the US | All | VRF multisplit system | SEER2 = 13.4 | AHRI 210/240 |
|  |  |  |  | 10.3 EER |  |
|  | ≥ 65,000 Btu/h and < 135,000 Btu/h |  |  | 14.6 IEER |  |
| VRF multisplit system with | 10.1 EER |
| VRF air cooled (cooling mode) |  | Electric resistance (or none) | heat recovery | 14.4 IEER | AHRI 1230 |
| ≥ 135,000 Btu/h and < 240,000 Btu/h | VRF multisplit system | 9.9 EER  14.4 IEER |
| VRF multisplit system with | 9.7 EER |
|  |  |  | heat recovery | 13.9 IEER |  |
|  |  |  | VRF multisplit system | 9.1 EER |  |
|  | ≥ 240,000 Btu/h |  | 12.7 IEER |  |
| VRF multisplit system with | 8.9 EER |
|  |  |  | heat recovery | 12.5 IEER |  |
|  |  | All | VRF multisplit systems | 12.0 EER | AHRI 1230 |
|  |  | 86°F entering water | 16.0 IEER |
|  | < 65,000 Btu/h |
| VRF multisplit systems with heat recovery  86°F entering water | 11.8 EER  15.8 IEER |
|  |  | VRF multisplit system | 12.0 EER |
|  |  | 86°F entering water | 16.0 IEER |
| VRF water source | ≥ 65,000 Btu/h and < 135,000 Btu/h |  |  |
| VRF multisplit system with heat recovery  86°F entering water | 11.8 EER  15.8 IEER |
| (cooling mode) |
|  | VRF multisplit system | 10.0 EER |
|  |  | 86°F entering water | 14.0 IEER |
|  | ≥ 135,000 Btu/h and < 240,000 Btu/h |  |  |
| VRF multisplit system with heat recovery  86°F entering water | 9.8 EER  13.8 IEER |
|  |  | VRF multisplit system | 10.0 EER |
|  |  | 86°F entering water | 12.0 IEER |
|  | ≥ 240,000 Btu/h |  |  |
| VRF multisplit system with heat recovery  86°F entering water | 9.8 EER  11.8 IEER |

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| **TABLE C403.3.2(9)—ELECTRICALLY OPERATED**  **VARIABLE-REFRIGERANT-FLOW AND APPLIED HEAT PUMPS—MINIMUM EFFICIENCY REQUIREMENTS—continued** | | | | | |
| **EQUIPMENT TYPE** | **SIZE CATEGORY** | **HEATING SECTION TYPE** | **SUBCATEGORY OR RATING CONDITION** | **MINIMUM EFFICIENCY** | **TEST PROCEDUREa** |
| VRF groundwater source (cooling mode) | < 135,000 Btu/h | All | VRF multisplit system 59°F entering water | 16.2 EER | AHRI 1230 |
| VRF multisplit system with heat recovery  59°F entering water | 16.0 EER |
| ≥ 135,000 Btu/h | VRF multisplit system 59°F entering water | 13.8 EER |
| VRF multisplit system with heat recovery  59°F entering water | 13.6 EER |
| VRF ground source (cooling mode) | < 135,000 Btu/h | All | VRF multisplit system 77°F entering water | 13.4 EER | AHRI 1230 |
| VRF multisplit system with heat recovery  77°F entering water | 13.2 EER |
| ≥ 135,000 Btu/h | VRF multisplit system 77°F entering water | 11.0 EER |
| VRF multisplit system with heat recovery  77°F entering water | 10.8 EER |
| VRF air cooled (heating mode) | < 65,000 Btu/h (cooling capacity) three-phase for applications in the US and single- and three-phase for applications outside the US | VRF multisplit system | HSPF2 = 7.5 | AHRI 210/240 |
| ≥ 65,000 Btu/h and < 135,000 Btu/h (cooling capacity) | VRF multisplit system 47°F db/43°F wb outdoor air | 3.3 COPH | AHRI 1230 |
| 17°F db/15°F wb outdoor air | 2.25 COPH |
| ≥ 135,000 Btu/h (cooling capacity) | VRF multisplit system 47°F db/43°F wb outdoor air | 3.2 COPH |
| 17°F db/15°F wb outdoor air | 2.05 COPH |
| VRF water source (heating mode) | < 65,000 Btu/h (cooling capacity) | VRF multisplit system 68°F entering water | 4.3 COPH | AHRI 1230 |
| ≥ 65,000 Btu/h and < 135,000 Btu/h (cooling capacity) | VRF multisplit system 68°F entering water | 4.3 COPH |
| ≥ 135,000 Btu/h and < 240,000 Btu/h (cooling capacity) | VRF multisplit system 68°F entering water | 4.0 COPH |
| ≥ 240,000 Btu/h (cooling capacity) | VRF multisplit system 68°F entering water | 3.9 COPH |
| VRF groundwater source (heating mode) | < 135,000 Btu/h (cooling capacity) | VRF multisplit system 50°F entering water | 3.6 COPH | AHRI 1230 |
| ≥ 135,000 Btu/h (cooling capacity) | VRF multisplit system 50°F entering water | 3.3 COPH |
| VRF ground source (heating mode) | < 135,000 Btu/h (cooling capacity) | VRF multisplit system 32°F entering water | 3.1 COPH | AHRI 1230 |
| ≥ 135,000 Btu/h (cooling capacity) | VRF multisplit system 32°F entering water | 2.8 COPH |
| For SI: °C = (°F – 32)/1.8, 1 British thermal unit per hour = 0.2931 W, db = dry bulb temperature, wb = wet bulb temperature.  a. Chapter 6 contains a complete specification of the referenced standards, which include test procedures, including the reference year version of the test procedure. | | | | | |

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| **TABLE C403.3.2(10)—FLOOR-MOUNTED AIR CONDITIONERS AND CONDENSING UNITS SERVING COMPUTER ROOMS—MINIMUM EFFICIENCY REQUIREMENTS** | | | | | |
| **EQUIPMENT TYPE** | **STANDARD MODEL** | **NET SENSIBLE COOLING CAPACITY** | **MINIMUM NET SENSIBLE COP** | **RATING CONDITIONS RETURN AIR**  **(dry bulb/dew point)** | **TEST PROCEDURE** |
| Air cooled | Downflow | < 80,000 Btu/h | 2.70 | 85°F/52°F (Class 2) | AHRI 1360 |
| ≥ 80,000 Btu/h and  < 295,000 Btu/h | 2.58 |
| ≥ 295,000 Btu/h | 2.36 |
| Upflow—ducted | < 80,000 Btu/h | 2.67 |
| ≥ 80,000 Btu/h and  < 295,000 Btu/h | 2.55 |
| ≥ 295,000 Btu/h | 2.33 |
| Upflow—nonducted | < 65,000 Btu/h | 2.16 | 75°F/52°F (Class 1) |
| ≥ 65,000 Btu/h and  < 240,000 Btu/h | 2.04 |
| ≥ 240,000 Btu/h | 1.89 |
| Horizontal | < 65,000 Btu/h | 2.65 | 95°F/52°F (Class 3) |
| ≥ 65,000 Btu/h and  < 240,000 Btu/h | 2.55 |
| ≥ 240,000 Btu/h | 2.47 |
| Air cooled with fluid economizer | Downflow | < 80,000 Btu/h | 2.70 | 85°F/52°F (Class 1) | AHRI 1360 |
| ≥ 80,000 Btu/h and  < 295,000 Btu/h | 2.58 |
| ≥ 295,000 Btu/h | 2.36 |
| Upflow—ducted | < 80,000 Btu/h | 2.67 |
| ≥ 80,000 Btu/h and  < 295,000 Btu/h | 2.55 |
| ≥ 295,000 Btu/h | 2.33 |
| Upflow—nonducted | < 65,000 Btu/h | 2.09 | 75°F/52°F (Class 1) |
| ≥ 65,000 Btu/h and  < 240,000 Btu/h | 1.99 |
| ≥ 240,000 Btu/h | 1.81 |
| Horizontal | < 65,000 Btu/h | 2.65 | 95°F/52°F (Class 3) |
| ≥ 65,000 Btu/h and  < 240,000 Btu/h | 2.55 |
| ≥ 240,000 Btu/h | 2.47 |
| Water cooled | Downflow | < 80,000 Btu/h | 2.82 | 85°F/52°F (Class 1) | AHRI 1360 |
| ≥ 80,000 Btu/h and  < 295,000 Btu/h | 2.73 |
| ≥ 295,000 Btu/h | 2.67 |
| Upflow—ducted | < 80,000 Btu/h | 2.79 |
| ≥ 80,000 Btu/h and  < 295,000 Btu/h | 2.70 |
| ≥ 295,000 Btu/h | 2.64 |
| Upflow—nonducted | < 65,000 Btu/h | 2.43 | 75°F/52°F (Class 1) |
| ≥ 65,000 Btu/h and  < 240,000 Btu/h | 2.32 |
| ≥ 240,000 Btu/h | 2.20 |
| Horizontal | < 65,000 Btu/h | 2.79 | 95°F/52°F (Class 3) |
| ≥ 65,000 Btu/h and  < 240,000 Btu/h | 2.68 |
| ≥ 240,000 Btu/h | 2.60 |

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| **TABLE C403.3.2(10)—FLOOR-MOUNTED AIR CONDITIONERS AND**  **CONDENSING UNITS SERVING COMPUTER ROOMS—MINIMUM EFFICIENCY REQUIREMENTS—continued** | | | | | |
| **EQUIPMENT TYPE** | **STANDARD MODEL** | **NET SENSIBLE COOLING CAPACITY** | **MINIMUM NET SENSIBLE COP** | **RATING CONDITIONS RETURN AIR**  **(dry bulb/dew point)** | **TEST PROCEDURE** |
| Water cooled with fluid economizer | Downflow | < 80,000 Btu/h | 2.77 | 85°F/52°F (Class 1) | AHRI 1360 |
| ≥ 80,000 Btu/h and  < 295,000 Btu/h | 2.68 |
| ≥ 295,000 Btu/h | 2.61 |
| Upflow—ducted | < 80,000 Btu/h | 2.74 |
| ≥ 80,000 Btu/h and  < 295,000 Btu/h | 2.65 |
| ≥ 295,000 Btu/h | 2.58 |
| Upflow—nonducted | < 65,000 Btu/h | 2.35 | 75°F/52°F (Class 1) |
| ≥ 65,000 Btu/h and  < 240,000 Btu/h | 2.24 |
| ≥ 240,000 Btu/h | 2.12 |
| Horizontal | < 65,000 Btu/h | 2.71 | 95°F/52°F (Class 3) |
| ≥ 65,000 Btu/h and  < 240,000 Btu/h | 2.60 |
| ≥ 240,000 Btu/h | 2.54 |
| Glycol cooled | Downflow | < 80,000 Btu/h | 2.56 | 85°F/52°F (Class 1) | AHRI 1360 |
| ≥ 80,000 Btu/h and  < 295,000 Btu/h | 2.24 |
| ≥ 295,000 Btu/h | 2.21 |
| Upflow—ducted | < 80,000 Btu/h | 2.53 |
| ≥ 80,000 Btu/h and  < 295,000 Btu/h | 2.21 |
| ≥ 295,000 Btu/h | 2.18 |
| Upflow, nonducted | < 65,000 Btu/h | 2.08 | 75°F/52°F (Class 1) |
| ≥ 65,000 Btu/h and  < 240,000 Btu/h | 1.90 |
| ≥ 240,000 Btu/h | 1.81 |
| Horizontal | < 65,000 Btu/h | 2.48 | 95°F/52°F (Class 3) |
| ≥ 65,000 Btu/h and  < 240,000 Btu/h | 2.18 |
| ≥ 240,000 Btu/h | 2.18 |
| Glycol cooled with fluid economizer | Downflow | < 80,000 Btu/h | 2.51 | 85°F/52°F (Class 1) | AHRI 1360 |
| ≥ 80,000 Btu/h and  < 295,000 Btu/h | 2.19 |
| ≥ 295,000 Btu/h | 2.15 |
| Upflow—ducted | < 80,000 Btu/h | 2.48 |
| ≥ 80,000 Btu/h and  < 295,000 Btu/h | 2.16 |
| ≥ 295,000 Btu/h | 2.12 |
| Upflow—nonducted | < 65,000 Btu/h | 2.00 | 75°F/52°F (Class 1) |
| ≥ 65,000 Btu/h and  < 240,000 Btu/h | 1.82 |
| ≥ 240,000 Btu/h | 1.73 |
| Horizontal | < 65,000 Btu/h | 2.44 | 95°F/52°F (Class 3) |
| ≥ 65,000 Btu/h and  < 240,000 Btu/h | 2.10 |
| ≥ 240,000 Btu/h | 2.10 |
| For SI: 1 British thermal unit per hour = 0.2931 W, °C = (°F – 32)/1.8, COP = (Btu/h × hp)/(2,550.7). | | | | | |

|  |  |  |  |
| --- | --- | --- | --- |
| **TABLE C403.3.2(11)—VAPOR-COMPRESSION-BASED INDOOR POOL DEHUMIDIFIERS—MINIMUM EFFICIENCY REQUIREMENTS** | | | |
| **EQUIPMENT TYPE** | **SUBCATEGORY OR RATING CONDITION** | **MINIMUM EFFICIENCY** | **TEST PROCEDURE** |
| Single package indoor (with or without economizer) | Rating conditions: A or C | 3.5 MRE | AHRI 910 |
| Single package indoor water-cooled (with or without economizer) | Rating conditions: A, B or C | 3.5 MRE |
| Single package indoor air-cooled (with or without economizer) | Rating conditions: A, B or C | 3.5 MRE |
| Split system indoor air-cooled (with or without economizer) | Rating conditions: A, B or C | 3.5 MRE |

|  |  |  |  |
| --- | --- | --- | --- |
| **TABLE C403.3.2(12)—ELECTRICALLY OPERATED DX-DOAS UNITS, SINGLE-PACKAGE AND REMOTE CONDENSER, WITHOUT ENERGY RECOVERY—MINIMUM EFFICIENCY REQUIREMENTS** | | | |
| **EQUIPMENT TYPE** | **SUBCATEGORY OR RATING CONDITION** | **MINIMUM EFFICIENCY** | **TEST PROCEDUREa** |
| Air cooled (dehumidification mode) | — | 3.8 ISMRE2 | AHRI 920 |
| Air-source heat pumps (dehumidification mode) | — | 3.8 ISMRE2 | AHRI 920 |
| Water cooled (dehumidification mode) | Cooling tower condenser water | 4.7 ISMRE2 | AHRI 920 |
| Air-source heat pump (heating mode) | — | 2.05 ISCOP2 | AHRI 920 |
| Water-source heat pump (dehumidification mode) | Ground source, closed and open loopb | 4.6 ISMRE2 | AHRI 920 |
| Water source | 3.8 ISMRE2 |
| Water-source heat pump (heating mode) | Ground source, closed and open loopb | 2.13 ISCOP2 | AHRI 920 |
| Water source | 2.13 ISCOP2 |
| 1. Chapter 6 contains a complete specification of the referenced standards, which include test procedures, including the reference year version of the test procedure. 2. Open-loop systems are rated using closed-loop test conditions. | | | |

|  |  |  |  |
| --- | --- | --- | --- |
| **TABLE C403.3.2(13)—ELECTRICALLY OPERATED DX-DOAS UNITS, SINGLE-PACKAGE AND REMOTE CONDENSER, WITH ENERGY RECOVERY—MINIMUM EFFICIENCY REQUIREMENTS** | | | |
| **EQUIPMENT TYPE** | **SUBCATEGORY OR RATING CONDITION** | **MINIMUM EFFICIENCY** | **TEST PROCEDUREa** |
| Air cooled (dehumidification mode) | — | 5.0 ISMRE2 | AHRI 920 |
| Air-source heat pumps (dehumidification mode) | — | 5.0 ISMRE2 | AHRI 920 |
| Water cooled (dehumidification mode) | Cooling tower condenser water | 5.1 ISMRE2 | AHRI 920 |
| Air-source heat pump (heating mode) | — | 3.2 ISCOP2 | AHRI 920 |
| Water-source heat pump (dehumidification mode) | Ground source, closed and open loopb | 5.0 ISMRE2 | AHRI 920 |
| Water source | 4.6 ISMRE2 |
| Water-source heat pump (heating mode) | Ground source, closed and open loopb | 3.5 ISCOP2 | AHRI 920 |
| Water source | 4.04 ISCOP2 |
| 1. Chapter 6 contains a complete specification of the referenced standards, which include test procedures, including the reference year version of the test procedure. 2. Open-loop systems are rated using closed-loop test conditions. | | | |

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| **TABLE C403.3.2(14)—ELECTRICALLY OPERATED WATER-SOURCE HEAT PUMPS—MINIMUM EFFICIENCY REQUIREMENTSb** | | | | | |
| **EQUIPMENT TYPE** | **SIZE CATEGORY** | **HEATING SECTION TYPE** | **SUBCATEGORY OR RATING CONDITION** | **MINIMUM EFFICIENCY** | **TEST PROCEDUREa** |
| Water-to-air, water loop (cooling mode) | < 17,000 Btu/h | All | 86°F entering water | 12.2 EER | ISO 13256-1 |
| ≥ 17,000 Btu/h and  < 65,000 Btu/h | 13.0 EER |
| ≥ 65,000 Btu/h and  < 135,000 Btu/h | 13.0 EER |
| Water-to-air, ground water (cooling mode) | < 135,000 Btu/h | All | 59°F entering water | 18.0 EER | ISO 13256-1 |
| Brine-to-air, ground loop (cooling mode) | < 135,000 Btu/h | All | 77°F entering water | 14.1 EER | ISO 13256-1 |
| Water-to-water, water loop (cooling mode) | < 135,000 Btu/h | All | 86°F entering water | 10.6 EER | ISO 13256-2 |
| Water-to-water, ground water (cooling mode) | < 135,000 Btu/h | All | 59°F entering water | 16.3 EER | ISO 13256-2 |
| Brine-to-water, ground loop (cooling mode) | < 135,000 Btu/h | All | 77°F entering water | 12.1 EER | ISO 13256-2 |
| Water-to-water, water loop (heating mode) | < 135,000 Btu/h (cooling capacity) | — | 68°F entering water | 4.3 COPH | ISO 13256-1 |
| Water-to-air, ground water (heating mode) | < 135,000 Btu/h (cooling capacity) | — | 50°F entering water | 3.7 COPH | ISO 13256-1 |
| Brine-to-air, ground loop (heating mode) | < 135,000 Btu/h (cooling capacity) | — | 32°F entering water | 3.2 COPH | ISO 13256-1 |
| Water-to-water, water loop (heating mode) | < 135,000 Btu/h (cooling capacity) | — | 68°F entering water | 3.7 COPH | ISO 13256-1 |
| Water-to-water, ground water (heating mode) | < 135,000 Btu/h (cooling capacity) | — | 50°F entering water | 3.1 COPH | ISO 13256-2 |
| Brine-to-water, ground loop (heating mode) | < 135,000 Btu/h (cooling capacity) | — | 32°F entering water | 2.5 COPH | ISO 13256-2 |
| For SI: 1 British thermal unit per hour = 0.2931 W, °C = (°F – 32)/1.8.   1. Chapter 6 contains a complete specification of the referenced standards, which include test procedures, including the reference year version of the test procedure. 2. Single-phase, US air-cooled heat pumps < 65,000 Btu/h are regulated as consumer products by 10 CFR 430. SEER, SEER2, HPSF and HPSF2 values for single-phase products are set by the US DOE. Informative Note: See ASHRAE 90.1 Informative Appendix F for the US DOE minimum. | | | | | |

**COMMERCIAL ENERGY EFFICIENCY**

**2024 INTERNATIONAL ENERGY CONSERVATION CODE®**

**103**

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE C403.3.2(15)—HEAT-PUMP AND HEAT RECOVERY CHILLER PACKAGES—MINIMUM EFFICIENCY REQUIREMENTSg, o** | | | | | | | | | | | | | | | | | |
| **HEATING OPERATION EFFICIENCYb, e, j** | | | | | | | | | | | | | | | | | |
| **EQUIPMENT TYPE** | **SIZE CATEGORY REFRIGERATING CAPACITYn, tonR** | **COOLING OPERATION EFFICIENCY a, d ,e, j AIR-SOURCE EER (FL/IPLV), Btu/W × h LIQUID- SOURCE POWER INPUT PER CAPACITY (FL/IPLV), kW/tonR** | | **HEATING SOURCE CONDITIONS**  **(leaving liquid) OR OUTDOOR AIR TEMPERATURE**  **(db/wb), °F** | **HEAT-PUMP HEATING FULL-LOAD HEATING EFFICIENCY (COPH)f, h, k, W/W** | | | | **SIMULTANEOUS COOLING AND HEATING FULL-LOAD EFFICIENCY (COPSHC)b, i, W/W** | | | | **HEAT RECOVERY HEATING FULL-LOAD EFFICIENCY (COPHR)c, j, W/W** | | | | **Test Procedurea** |
| **Entering/Leaving Heating Liquid Temperature** | | | | **Entering/Leaving Heating Liquid Temperature** | | | | **Entering/Leaving Heating Liquid Temperature** | | | |
| **Low** | **Medium** | **High** | **Boost** | **Low** | **Medium** | **High** | **Boost** | **Low** | **Medium** | **Hot- Water 1** | **Hot- Water 2** |
| **Path A** | **Path B** | **95°F/**  **105°F** | **105°F/**  **120°F** | **120°F/**  **140°F** | **120°F/**  **140°F** | **95°F/**  **105°F** | **105°F/**  **120°F** | **120°F/**  **140°F** | **120°F/**  **140°F** | **95°F/**  **105°F** | **105°F/**  **120°F** | **90°F/**  **140°F** | **120°F/**  **140°F** |
| Air source | < 150.0 | ≥ 9.595 FL  ≥ 13.02 IPLV.IP | ≥ 9.215 FL  ≥ 15.01 IPLV.IP | 47 db  43 wbl | ≥ 3.290 | ≥ 2.770 | ≥ 2.310 | NA | NA | NA | NA | NA | NA | NA | NA | NA | AHRI 550/590 |
| 17 db  15 wbl | ≥ 2.029 | ≥ 1.775 | ≥ 1.483 | NA | NA | NA | NA | NA | NA | NA | NA | NA |
| ≥ 150.0 | ≥ 9.595 FL  ≥ 13.30 IPLV.IP | ≥ 9.215 FL  ≥ 15.30 IPLV.IP | 47 db  43 wbl | ≥ 3.290 | ≥ 2.770 | ≥ 2.310 | NA | NA | NA | NA | NA | NA | NA | NA | NA |
| 17 db  15 wbl | ≥ 2.029 | ≥ 1.775 | ≥ 1.483 | NA | NA | NA | NA | NA | NA | NA | NA | NA |
| Liquid- source electrically operated positive displace- ment | ≥ 11.25p and < 150 | ≤ 0.7895 FL  ≤ 0.6316 IPLV.IP | ≤ 0.8211 FL  ≤ 0.5263 IPLV.IP | 44m | ≥ 4.640 | ≥ 3.680 | ≥ 2.680 | NA | ≥ 8.330 | ≥ 6.410 | ≥ 4.420 | NA | ≥ 8.330 | ≥ 6.410 | ≥ 4.862 | ≥ 4.420 | AHRI 550/590 |
| 65m | NA | NA | NA | ≥ 3.550 | NA | NA | NA | ≥ 6.150 | NA | NA | NA | NA |
| ≥ 150 and < 300 | ≤ 0.7579 FL  ≤ 0.5895 IPLV.IP | ≤ 0.7895 FL  ≤ 0.5158 IPLV.IP | 44m | ≥ 4.640 | ≥ 3.680 | ≥ 2.680 | NA | ≥ 8.330 | ≥ 6.410 | ≥ 4.420 | NA | ≥ 8.330 | ≥ 6.410 | ≥ 4.862 | ≥ 4.420 |
| 65m | NA | NA | NA | ≥ 3.550 | NA | NA | NA | ≥ 6.150 | NA | NA | NA | NA |
| ≥ 300 and < 400 | ≤ 0.6947 FL  ≤ 0.5684 IPLV.IP | ≤ 0.7158 FL  ≤ 0.4632 IPLV.IP | 44m | ≥ 4.640 | ≥ 3.680 | ≥ 2.680 | NA | ≥ 8.330 | ≥ 6.410 | ≥ 4.420 | NA | ≥ 8.330 | ≥ 6.410 | ≥ 4.862 | ≥ 4.420 |
| 65m | NA | NA | NA | ≥ 3.550 | NA | NA | NA | ≥ 6.150 | NA | NA | NA | NA |
| ≥ 400 and < 600 | ≤ 0.6421 FL  ≤ 0.5474 IPLV.IP | ≤ 0.6579 FL  ≤ 0.4316 IPLV.IP | 44m | ≥ 4.930 | ≥ 3.960 | ≥ 2.970 | NA | ≥ 8.900 | ≥ 6.980 | ≥ 5.000 | NA | ≥ 8.900 | ≥ 6.980 | ≥ 5.500 | ≥ 5.000 |
| 65m | NA | NA | NA | ≥ 3.900 | NA | NA | NA | ≥ 6.850 | NA | NA | NA | NA |
| ≥ 600 | ≤ 0.5895 FL  ≤ 0.5263 IPLV.IP | ≤ 0.6158 FL  ≤ 0.4000 IPLV.IP | 44m | ≥ 4.930 | ≥ 3.960 | ≥ 2.970 | NA | ≥ 8.900 | ≥ 6.980 | ≥ 5.000 | NA | ≥ 8.900 | ≥ 6.980 | ≥ 5.500 | ≥ 5.000 |
| 65m | NA | NA | NA | ≥ 3.900 | NA | NA | NA | ≥ 6.850 | NA | NA | NA | NA |
| Liquid- source electrically operated centrifugal | ≥11.25p and <150 | ≤ 0.6421 FL  ≤ 0.5789 IPLV.IP | ≤ 0.7316 FL  ≤ 0.4632 IPLV.IP | 44m | ≥ 4.640 | ≥ 3.680 | ≥ 2.680 | NA | ≥ 8.330 | ≥ 6.410 | ≥ 4.420 | NA | ≥ 8.330 | ≥ 6.410 | ≥ 4.862 | ≥ 4.420 | AHRI 550/590 |
| 65m | NA | NA | NA | ≥ 3.550 | NA | NA | NA | ≥ 6.150 | NA | NA | NA | NA |
| ≥ 150 and < 300 | ≤ 0.6190 FL  ≤ 0.5748 IPLV.IP | ≤ 0.6684 FL  ≤ 0.4211 IPLV.IP | 44m | ≥ 4.640 | ≥ 3.680 | ≥ 2.680 | NA | ≥ 8.330 | ≥ 6.410 | ≥ 4.420 | NA | ≥ 8.330 | ≥ 6.410 | ≥ 4.862 | ≥ 4.420 |
| 65m | NA | NA | NA | ≥ 3.550 | NA | NA | NA | ≥ 6.150 | NA | NA | NA | NA |
| ≥ 300 and < 400 | ≤ 0.5895 FL  ≤ 0.5526 IPLV.IP | ≤ 0.6263 FL  ≤ 0.4105 IPLV.IP | 44m | ≥ 4.640 | ≥ 3.680 | ≥ 2.680 | NA | ≥ 8.330 | ≥ 6.410 | ≥ 4.420 | NA | ≥ 8.330 | ≥ 6.410 | ≥ 4.862 | ≥ 4.420 |
| 65m | NA | NA | NA | ≥ 3.550 | NA | NA | NA | ≥ 6.150 | NA | NA | NA | NA |
| ≥ 400 and < 600 | ≤ 0.5895 FL  ≤ 0.5263 IPLV.IP | ≤ 0.6158 FL  ≤ 0.4000 IPLV.IP | 44m | ≥ 4.930 | ≥ 3.960 | ≥ 2.970 | NA | ≥ 8.900 | ≥ 6.980 | ≥ 5.000 | NA | ≥ 8.900 | ≥ 6.980 | ≥ 5.500 | ≥ 5.000 |
| 65m | NA | NA | NA | ≥ 3.900 | NA | NA | NA | ≥ 6.850 | NA | NA | NA | NA |
| ≥ 60 | ≤ 0.5895 FL  ≤ 0.5263 IPLV.IP | ≤ 0.6158 FL  ≤ 0.4000 IPLV.IP | 44m | ≥ 4.930 | ≥ 3.960 | ≥ 2.970 | NA | ≥ 8.900 | ≥ 6.980 | ≥ 5.000 | NA | ≥ 8.900 | ≥ 6.980 | ≥ 5.500 | ≥ 5.000 |
| 65m | NA | NA | NA | ≥ 3.900 | NA | NA | NA | ≥ 6.850 | NA | NA | NA | NA |

**COMMERCIAL ENERGY EFFICIENCY**

**104**

**2024 INTERNATIONAL ENERGY CONSERVATION CODE®**

**TABLE C403.3.2(15)—HEAT-PUMP AND HEAT RECOVERY CHILLER PACKAGES—MINIMUM EFFICIENCY REQUIREMENTSg, o—continued**

For SI: °C = (°F – 32)/1.8.

NA = Not Applicable.

1. Cooling rating conditions are standard rating conditions defined in AHRI 550/590 (I-P), Table 4, except for liquid-cooled centrifugal chilling packages which can adjust cooling efficiency for nonstandard rating conditions using Kadj proce- dure in accordance with ASHRAE 90.1 Section 6.4.1.2.1.
2. Heating full-load rating conditions are at standard rating conditions defined in AHRI 550/590 (I-P), Table 4; includes the impact of defrost for air source heating ratings.
3. For liquid-source heat recovery chilling packages that have capabilities for heat rejection to a heat recovery condenser and a tower condenser the COPHR applies to operation at full load with 100 percent heat recovery (no tower rejec- tion). Units that only have capabilities for partial heat recovery shall meet the requirements of ASHRAE 90.1 Table 6.8.1-3.
4. For cooling operation, compliance with both the FL and IPLV is required, but only compliance with Path A or Path B cooling efficiency is required.
5. For units that operate in both cooling and heating, compliance with both the cooling and heating efficiency is required.
6. For applications where the chilling package is installed to operate only in heating, compliance only with the heating performance COPH is required at only one of the heating AHRI 550/590 (I-P) standard rating conditions of Low, Medium, High, or Boost. Compliance with cooling performance is not required.
7. For air source heat pumps, compliance with both the 47°F and 17°F heating source outdoor air temperature (OAT) rating efficiency is required for heating.
8. For heat-pump chilling package applications where the cooling capacity is not being used for conditioning, compliance with the heating performance COPH is only required at one of the four heating AHRI 550/590 standard ratings condi- tions of Low, Medium, High, or Boost. Compliance with the cooling performance is required as defined in notes a and d, except as noted in note f.
9. For simultaneous cooling and heating chillers applications where there is simultaneous cooling and heating, compliance with the simultaneous cooling performance heat recovery COPSHC is only required at one of the four simultaneous cooling and heating AHRI 550/590 (I-P) standard ratings conditions of Low, Medium, High, or Boost. Compliance with the cooling only performance is required as defined in notes a and d.
10. For heat recovery heating chilling package applications where there is simultaneous cooling and heating, compliance with the heating performance heat recovery COPHR is only required at one of the four heating AHRI 550/590 (I-P) stan- dard ratings conditions of Low, Medium, Hot-Water 1, or Hot-Water 2. Compliance with the cooling only performance is required as defined in notes a and d.
11. Chilling packages employing a freeze-protection liquid in accordance with ASHRAE 90.1 Section 6.4.1.2.2 shall be tested or rated with water for the purpose of compliance with the requirements of this table.
12. Outdoor air entering dry-bulb (db) temperature and wet-bulb (wb) temperature.
13. Source-leaving liquid temperature.
    * The cooling evaporator liquid flow rate used for the heating rating for a reverse cycle air-to-water heat pump shall be the flow rate determined during the full-load cooling rating.
    * The cooling evaporator liquid flow rate for the simultaneous cooling and heating and heat recovery liquid cooled chilling packages rating shall be the liquid flow rates from the cooling operation full load rating.
    * For heating-only fluid-to-fluid chiller packages, the evaporator flow rate obtained with an entering liquid temperature of 54°F and a leaving liquid temperature of 44°F shall be used.
14. The size category is the full-load net refrigerating cooling mode capacity, which is the capacity of the evaporator available for cooling of the thermal load external to the chilling package.
15. A heat recovery condenser at its maximum load point must remove enough heat from the refrigerant to cool the refrigerant to remove all superheat energy and begin condensation of the refrigerant. A heat recovery system where only the superheat is reduced is not covered by ASHRAE 90.1 Table 6.8.1-16 and is considered a desuperheater, and the chiller package must comply with ASHRAE 90.1 Table 6.8.1-3.
16. Water-to-water heat pumps with a capacity less than 135,000 Btu/h are covered by ASHRAE 90.1 Table 6.8.1-15.

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| **TABLE C403.3.2(16)—**  **CEILING-MOUNTED COMPUTER ROOM AIR CONDITIONERS—MINIMUM EFFICIENCY REQUIREMENTS** | | | | | |
| **EQUIPMENT TYPE** | **STANDARD MODEL** | **NET SENSIBLE COOLING CAPACITY** | **MINIMUM NET SENSIBLE COP** | **RATING CONDITIONS RETURN AIR**  **(dry bulb/dew point)** | **TEST PROCEDUREa** |
| Air cooled with free air discharge condenser | Ducted | < 29,000 Btu/h | 2.05 | 75°F/52°F (Class 1) | AHRI 1360 |
| ≥ 29,000 Btu/h and  < 65,000 Btu/h | 2.02 |
| ≥ 65,000 Btu/h | 1.92 |
| Nonducted | < 29,000 Btu/h | 2.08 |
| ≥ 29,000 Btu/h and  < 65,000 Btu/h | 2.05 |
| ≥ 65,000 Btu/h | 1.94 |
| Air cooled with free air discharge condenser with fluid economizer | Ducted | < 29,000 Btu/h | 2.01 | 75°F/52°F (Class 1) | AHRI 1360 |
| ≥ 29,000 Btu/h and  < 65,000 Btu/h | 1.97 |
| ≥ 65,000 Btu/h | 1.87 |
| Nonducted | < 29,000 Btu/h | 2.04 |
| ≥ 29,000 Btu/h and  < 65,000 Btu/h | 2.00 |
| ≥ 65,000 Btu/h | 1.89 |
| Air cooled with ducted condenser | Ducted | < 29,000 Btu/h | 1.86 | 75°F/52°F (Class 1) | AHRI 1360 |
| ≥ 29,000 Btu/h and  < 65,000 Btu/h | 1.83 |
| ≥ 65,000 Btu/h | 1.73 |
| Nonducted | < 29,000 Btu/h | 1.89 |
| ≥ 29,000 Btu/h and  < 65,000 Btu/h | 1.86 |
| ≥ 65,000 Btu/h | 1.75 |
| Air cooled with fluid economizer and ducted condenser | Ducted | < 29,000 Btu/h | 1.82 | 75°F/52°F (Class 1) | AHRI 1360 |
| ≥ 29,000 Btu/h and  < 65,000 Btu/h | 1.78 |
| ≥ 65,000 Btu/h | 1.68 |
| Nonducted | < 29,000 Btu/h | 1.85 |
| ≥ 29,000 Btu/h and  < 65,000 Btu/h | 1.81 |
| ≥ 65,000 Btu/h | 1.70 |
| Water cooled | Ducted | < 29,000 Btu/h | 2.38 | 75°F/52°F (Class 1) | AHRI 1360 |
| ≥ 29,000 Btu/h and  < 65,000 Btu/h | 2.28 |
| ≥ 65,000 Btu/h | 2.18 |
| Nonducted | < 29,000 Btu/h | 2.41 |
| ≥ 29,000 Btu/h and  < 65,000 Btu/h | 2.31 |
| ≥ 65,000 Btu/h | 2.20 |

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| **TABLE C403.3.2(16)—**  **CEILING-MOUNTED COMPUTER ROOM AIR CONDITIONERS—MINIMUM EFFICIENCY REQUIREMENTS—continued** | | | | | |
| **EQUIPMENT TYPE** | **STANDARD MODEL** | **NET SENSIBLE COOLING CAPACITY** | **MINIMUM NET SENSIBLE COP** | **RATING CONDITIONS RETURN AIR**  **(dry bulb/dew point)** | **TEST PROCEDUREa** |
| Water cooled with fluid economizer | Ducted | < 29,000 Btu/h | 2.33 | 75°F/52°F (Class 1) | AHRI 1360 |
| ≥ 29,000 Btu/h and  < 65,000 Btu/h | 2.23 |
| ≥ 65,000 Btu/h | 2.13 |
| Nonducted | < 29,000 Btu/h | 2.36 |
| ≥ 29,000 Btu/h and  < 65,000 Btu/h | 2.26 |
| ≥ 65,000 Btu/h | 2.16 |
| Glycol cooled | Ducted | < 29,000 Btu/h | 1.97 | 75°F/52°F (Class 1) | AHRI 1360 |
| ≥ 29,000 Btu/h and  < 65,000 Btu/h | 1.93 |
| ≥ 65,000 Btu/h | 1.78 |
| Nonducted | < 29,000 Btu/h | 2.00 |
| ≥ 29,000 Btu/h and  < 65,000 Btu/h | 1.98 |
| ≥ 65,000 Btu/h | 1.81 |
| Glycol cooled with fluid economizer | Ducted | < 29,000 Btu/h | 1.92 | 75°F/52°F (Class 1) | AHRI 1360 |
| ≥ 29,000 Btu/h and  < 65,000 Btu/h | 1.88 |
| ≥ 65,000 Btu/h | 1.73 |
| Nonducted | < 29,000 Btu/h | 1.95 |
| ≥ 29,000 Btu/h and  < 65,000 Btu/h | 1.93 |
| ≥ 65,000 Btu/h | 1.76 |
| For SI: 1 British thermal unit per hour = 0.2931 W, °C = (°F – 32)/1.8, COP = (Btu/h × hp)/(2,550.7).  a. Chapter 6 contains a complete specification of the referenced standards, which include test procedures, including the reference year version of the test procedure. | | | | | |

**C403.3.2.1 Water-cooled centrifugal chilling packages.** Equipment not designed for operation at AHRI Standard 550/590 test conditions of 44.00°F leaving and 54.00°F entering chilled-fluid temperatures, and with 85.00°F entering and 94.30°F leav- ing condenser-fluid temperatures, shall have maximum full-load kW/ton (FL) and part-load rating requirements adjusted using the following equations:

**Equation 4-5** *FLadj* = *FL/Kadj*

**Equation 4-6** *PLVadj* = *IPLV.IP/Kadj*

where:

*Kadj* = *A* × *B*

*FL* = Full-load kW/ton value from Table C403.3.2(3).

*FLadj* = Maximum full-load kW/ton rating, adjusted for nonstandard conditions.

*IPLV.IP* = *IPLV.IP* value from Table C403.3.2(3).

*PLVadj* = Maximum *NPLV* rating, adjusted for nonstandard conditions.

*A* = 0.00000014592 × (*LIFT*)4– 0.0000346496 × (*LIFT*)3+ 0.00314196 × ( *LIFT*)2– 0.147199 × (*LIFT*) + 3.93073

*B* = 0.0015 × *LvgE vap* + 0.934

*LIFT* = *LvgCond* – *LvgE vap*

*LvgCond* = Full-load condenser leaving fluid temperature (°F).

*LvgEvap* = Full-load evaporator leaving temperature (°F).

The *FLadj* and *PLVadj* values are applicable only for centrifugal chillers meeting all of the following full-load design ranges:

* 36.00°F ≤ *LvgE vap* ≤ 60.00°F
* *LvgCond* ≤ 115.00°F
* 20.00°F ≤ *LIFT* ≤ 80.00°F

Manufacturers shall calculate the *FLadj* and *PLV adj* before determining whether to label the chiller. Centrifugal chillers designed to operate outside of these ranges are not covered by this code.

**C403.3.2.2 Positive displacement (air- and water-cooled) chilling packages.** Equipment with a leaving fluid temperature higher than 32°F (0°C) and water-cooled positive displacement chilling packages with a condenser leaving fluid temperature below 115°F (46°C) shall meet the requirements of the tables in Section C403.3.2 when tested or certified with water at stan- dard rating conditions, in accordance with the referenced test procedure.

**C403.3.3 Hot gas bypass limitation.** Cooling systems shall not use hot gas bypass or other evaporator pressure control systems unless the system is designed with multiple steps of unloading or continuous capacity modulation. The capacity of the hot gas bypass shall be limited as indicated in Table C403.3.3, as limited by Section C403.5.1.

|  |  |
| --- | --- |
| **TABLE C403.3.3—MAXIMUM HOT GAS BYPASS CAPACITY** | |
| **RATED CAPACITY** | **MAXIMUM HOT GAS BYPASS CAPACITY (% of total capacity)** |
| ≤ 240,000 Btu/h | 50 |
| > 240,000 Btu/h | 25 |
| For SI: 1 British thermal unit per hour = 0.2931 W. | |

**C403.3.4 Boilers.** Boiler systems shall comply with the following:

1. Combustion air positive shutoff shall be provided on all newly installed boiler systems that meet one or more of the following conditions:
   1. The total input capacity is not less than 2,500,000 Btu/h (733 kW) and one or more of the boilers are designed to operate with a nonpositive vent static pressure.
   2. Any stack serving the *boiler system* is connected to two or more boilers with a total combined input capacity of not less than 2,500,000 Btu/h (733 kW).
2. Newly installed boilers or boiler systems with a combustion air fan motor *nameplate horsepower* rating of 10 horsepower (7.46 kW) or more shall comply with one of the following:
   1. The fan motor shall be variable speed.
   2. The fan motor shall include controls that modulate fan airflow as a function of the load to a speed 50 percent or less of design air volume.

**C403.3.4.1 Boiler oxygen concentration controls.** Newly installed boilers with an input capacity of 5,000,000 Btu/h (1465 kW) and steady state full-load less than 90 percent shall maintain stack-gas oxygen concentrations not greater than the values specified in Table C403.3.4.1. Combustion air volume shall be controlled with respect to measured flue gas oxygen concentra- tion. The use of a common gas and combustion air control linkage or jack shaft is not permitted.

**Exception:** These concentration limits do not apply where 50 percent or more of the *boiler system* capacity serves Group R- 2 occupancies.

|  |  |
| --- | --- |
| **TABLE C403.3.4.1—BOILER OXYGEN CONCENTRATIONS** | |
| **BOILER APPLICATION** | **MAXIMUM STACK-GAS OXYGEN CONCENTRATIONa** |
| Commercial boilers or where ≤ 10% of the boiler system capacity is used for process applications at design conditions | 5% |
| Process boilers | 3% |
| a. Concentration levels measured by volume on a dry basis over firing rates of 20 to 100 percent.  **Exception:** These concentration limits do not apply where 50 percent or more of the boiler system capacity serves Group R-2 occupancies. | |

**C403.3.4.2 Boiler turndown.** *Boiler systems* with design input of greater than 1,000,000 Btu/h (293 kW) shall comply with the turndown ratio specified in Table C403.3.4.2.

The system turndown requirement shall be met through the use of multiple single-input boilers, one or more *modulating boilers* or a combination of single-input and *modulating boilers*.

|  |  |
| --- | --- |
| **TABLE C403.3.4.2—BOILER TURNDOWN** | |
| **BOILER SYSTEM DESIGN INPUT (Btu/h)** | **MINIMUM TURNDOWN RATIO** |
| ≥ 1,000,000 and ≤ 5,000,000 | 3 to 1 |
| > 5,000,000 and ≤ 10,000,000 | 4 to 1 |
| > 10,000,000 | 5 to 1 |
| For SI: 1 British thermal unit per hour = 0.2931 W. | |

**C403.4 Heating and cooling system controls.** Heating and cooling system shall be provided with controls in accordance with Sections C403.4.1 through C403.4.8.

**C403.4.1 Thermostatic controls.** The supply of heating and cooling energy to each *zone* shall be controlled by individual ther- mostatic controls capable of responding to temperature within the *zone*. Where humidification or dehumidification or both is provided, not fewer than one humidity control device shall be provided for each humidity control system.

**Exception:** Independent perimeter systems that are designed to offset only *building thermal envelope* heat losses, gains or both serving one or more perimeter *zones* also served by an interior system provided that both of the following conditions are met:

1. The perimeter system includes not fewer than one thermostatic control *zone* for each *building* exposure having *exte- rior walls* facing only one orientation (within ±45 degrees) (0.8 rad) for more than 50 contiguous feet (15 240 mm).
2. The perimeter system heating and cooling supply is controlled by *thermostats* located within the *zones* served by the system.

**C403.4.1.1 Heat pump supplementary heat.** Heat pumps having supplementary electric resistance heat shall have controls that limit supplemental heat operation to only those times when one of the following applies:

1. The vapor compression cycle cannot provide the necessary heating energy to satisfy the *thermostat* setting.
2. The heat pump is operating in defrost mode.
3. The vapor compression cycle malfunctions.
4. The *thermostat* malfunctions.

**C403.4.1.2 Deadband.** Where used to control both heating and cooling, *zone* thermostatic controls shall:

1. Have separate setpoints for heating and cooling, each individually adjustable.
2. Be capable of and initially configured to provide a temperature range or deadband between the two setpoints of not less than 5°F (3°C) within which the supply of heating and cooling energy to the zone is shut off or reduced to a minimum.
3. Have a minimum deadband of not less than 1°F (0.56°C) when setpoints are adjusted.

Exceptions:

* 1. *Thermostats* requiring *manual* changeover between heating and cooling modes.
  2. Occupancies or applications where applicable codes or accreditation standards requiring precision in indoor temperature control shall be permitted to be initially configured to not less than 1°F (0.56°C) deadband.

**C403.4.1.3 Setpoint adjustment and display.** Where thermostatic control setpoints are capable of being adjusted by occu- pants or HVAC system operators, the adjustment shall be independent for the heating setpoint and the cooling setpoint; when one setpoint is changed, the other shall not change except as needed to maintain the minimum deadband required by Section C403.4.1.2. For thermostatic controls that display setpoints, both the heating and cooling setpoints shall be displayed simulta- neously, or the setpoint of the currently active mode (heating or cooling) shall be displayed along with an indication of that mode.

**C403.4.1.4 Setpoint overlap restriction.** Where heating and cooling to a *zone* are controlled by separate *zone* thermostatic controls located within the *zone*, mechanical or software means shall be provided to prevent the heating setpoint from exceeding the cooling setpoint, minus the deadband required by Section C403.4.1.2.

**C403.4.1.5 Heated or cooled vestibules.** The heating system for heated vestibules and air curtains with integral heating shall be provided with controls configured to shut off the source of heating when the outdoor air temperature is greater than 45°F (7°C). Vestibule heating and cooling systems shall be controlled by a *thermostat* located in the vestibule configured to limit heating to a temperature not greater than 60°F (16°C) and cooling to a temperature not less than 85°F (29°C).

**Exception:** Control of heating or cooling provided by site-recovered energy or transfer air that would otherwise be exhausted.

**C403.4.1.6 Hot water boiler outdoor temperature setback control.** Hot water boilers that supply heat to the *building* through one- or two-pipe heating systems shall have an outdoor setback control that lowers the boiler water temperature based on the outdoor temperature.

**C403.4.2 Off-hour controls.** Each *zone* shall be provided with thermostatic setback controls that are controlled by either an

*automatic* time clock or programmable control system.

Exceptions:

* + 1. *Zones* that will be operated continuously.
    2. *Zones* with a full HVAC load demand not exceeding 6,800 Btu/h (2 kW) and having a *manual* shutoff switch located with *ready access*.

**C403.4.2.1 Thermostatic setback.** Thermostatic setback controls shall be configured to set back or temporarily operate the system to maintain *zone* temperatures down to 55°F (13°C) or up to 85°F (29°C).

**C403.4.2.2 Automatic setback and shutdown.** *Automatic* time clock or programmable controls shall be capable of starting and stopping the system for seven different daily schedules per week and retaining their programming and time setting during a loss of power for not fewer than 10 hours. Additionally, the controls shall have a *manual* override that allows temporary oper- ation of the system for up to 2 hours; a manually operated timer configured to operate the system for up to 2 hours; or an occupancy sensor.

**C403.4.2.3 Optimum start and stop.** Optimum start and stop controls shall be provided for each heating and cooling system with direct control of individual *zones*. The optimum start controls shall be configured to automatically adjust the daily start time of the heating and cooling system in order to bring each space to the desired occupied temperature immediately prior to scheduled occupancy. The optimum stop controls shall be configured to reduce the heating and cooling system’s heating temperature setpoint and increase the cooling temperature setpoint by not less than 2°F (1.11°C) before scheduled unoccu- pied periods based on the thermal lag and acceptable drift in space temperature that is within comfort limits.

**Exception:** *Dwelling units* and *sleeping units* are not required to have optimum start controls.

**C403.4.3 Hydronic systems controls.** The heating of fluids that have been previously mechanically cooled and the cooling of fluids that have been previously mechanically heated shall be limited in accordance with Sections C403.4.3.1 through C403.4.3.3. Hydronic heating systems comprised of multiple-packaged boilers and designed to deliver conditioned water or steam into a common distribution system shall include *automatic* controls configured to sequence operation of the boilers. Hydronic heating systems composed of a single boiler and greater than 500,000 Btu/h (146.5 kW) input design capacity shall include either a multi- staged or modulating burner.

**C403.4.3.1 Three-pipe system.** Hydronic systems that use a common return system for both hot water and chilled water are prohibited.

**C403.4.3.2 Two-pipe changeover system.** Systems that use a common distribution system to supply both heated and chilled water shall be designed to allow a deadband between changeover from one mode to the other of not less than 15°F (8.3°C) outside air temperatures; be designed to and provided with controls that will allow operation in one mode for not less than 4 hours before changing over to the other mode; and be provided with controls that allow heating and cooling supply tempera- tures at the changeover point to be not more than 30°F (16.7°C) apart.

**C403.4.3.3 Hydronic (water loop) heat pump systems.** Hydronic heat pump systems shall comply with Sections C403.4.3.3.1 through C403.4.3.3.3.

**C403.4.3.3.1 Temperature deadband.** Hydronic heat pumps connected to a common heat pump water loop with central devices for heat rejection and heat addition shall have controls that are configured to provide a heat pump water supply temperature deadband of not less than 20°F (11°C) between initiation of heat rejection and heat addition by the central devices.

**Exception:** Where a system loop temperature optimization controller is installed and can determine the most efficient operating temperature based on real-time conditions of demand and capacity, deadbands of less than 20°F (11°C) shall be permitted.

**C403.4.3.3.2 Heat rejection.** The following shall apply to hydronic water loop heat pump systems in Climate Zones 3 through 8:

* + - 1. Where a closed-circuit cooling tower is used directly in the heat pump loop, either an *automatic* valve shall be installed to bypass the flow of water around the closed-circuit cooling tower, except for any flow necessary for freeze protection, or low-leakage positive-closure dampers shall be provided.
      2. Where an open-circuit cooling tower is used directly in the heat pump loop, an *automatic* valve shall be installed to bypass all heat pump water flow around the open-circuit cooling tower.
      3. Where an open-circuit or closed-circuit cooling tower is used in conjunction with a separate heat exchanger to isolate the open-circuit cooling tower from the heat pump loop, heat loss shall be controlled by shutting down the circulation pump on the cooling tower loop.

**Exception:** Where it can be demonstrated that a heat pump system will be required to reject heat throughout the year.

**C403.4.3.3.3 Two-position valve.** Each hydronic heat pump on the hydronic system having a total pump system power exceeding 10 hp (7.5 kW) shall have a two-position *automatic* valve interlocked to shut off the water flow when the compres- sor is off.

**C403.4.4 Part-load controls.** Hydronic systems greater than or equal to 300,000 Btu/h (87.9 kW) in design output capacity supplying heated or chilled water to comfort conditioning systems shall include controls that are configured to do all of the following:

1. Automatically reset the supply-water temperatures in response to varying *building* heating and cooling demand using coil valve position, zone-return water temperature, building-return water temperature or outside air temperature. The temperature shall be reset by not less than 25 percent of the design supply-to-return water temperature difference.
2. Automatically vary fluid flow for hydronic systems with a combined pump motor capacity of 2 hp (1.5 kW) or larger with three or more control valves or other devices by reducing the system design flow rate by not less than 50 percent or the maximum reduction allowed by the equipment manufacturer for proper operation of equipment by valves that modu- late or step open and close, or pumps that modulate or turn on and off as a function of load.
3. Automatically vary pump flow on heating-water systems, chilled-water systems and heat rejection loops serving water- cooled unitary air conditioners as follows:
   1. Where pumps operate continuously or operate based on a time schedule, pumps with nominal output motor power of 2 hp or more shall have a variable speed drive.
   2. Where pumps have *automatic direct digital control* configured to operate pumps only when zone heating or cooling is required, a variable speed drive shall be provided for pumps with motors having the same or greater nominal output power indicated in Table C403.4.4 based on the *climate zone* and system served.
4. Where a variable speed drive is required by Item 3 of this section, pump motor power input shall be not more than 30 percent of design wattage at 50 percent of the design water flow. Pump flow shall be controlled to maintain one control valve nearly wide open or to satisfy the minimum differential pressure.

Exceptions:

1. Supply-water temperature reset is not required for chilled-water systems supplied by off-site district chilled water or chilled water from ice storage systems.
2. Variable pump flow is not required on dedicated coil circulation pumps where needed for freeze protection.
3. Variable pump flow is not required on dedicated equipment circulation pumps where configured in primary/second- ary design to provide the minimum flow requirements of the equipment manufacturer for proper operation of equipment.
4. Variable speed drives are not required on heating water pumps where more than 50 percent of annual heat is gener- ated by an electric boiler.

|  |  |  |
| --- | --- | --- |
| **TABLE C403.4.4—VARIABLE SPEED DRIVE (VSD) REQUIREMENTS FOR DEMAND-CONTROLLED PUMPS** | | |
| **CHILLED WATER AND HEAT REJECTION LOOP PUMPS IN THESE CLIMATE ZONES** | **HEATING WATER PUMPS IN THESE CLIMATE ZONES** | **VSD REQUIRED FOR MOTORS WITH RATED OUTPUT OF:** |
| 0A, 0B, 1A, 1B, 2B | — | ≥ 2 hp |
| 2A, 3B | — | ≥ 3 hp |
| 3A, 3C, 4A, 4B | 7, 8 | ≥ 5 hp |
| 4C, 5A, 5B, 5C, 6A, 6B | 3C, 5A, 5C, 6A, 6B | ≥ 7.5 hp |
| — | 4A, 4C, 5B | ≥ 10 hp |
| 7, 8 | 4B | ≥ 15 hp |
| — | 2A, 2B, 3A, 3B | ≥ 25 hp |
| — | 0B, 1B | ≥ 100 hp |
| — | 0A, 1A | ≥ 200 hp |
| For SI: 1 hp = 0.746 kW. | | |

**C403.4.5 Pump isolation.** Chilled water plants including more than one chiller shall be capable of and configured to reduce flow automatically through the chiller plant when a chiller is shut down. Chillers piped in series for the purpose of increased tempera- ture differential shall be considered as one chiller.

Boiler systems including more than one boiler shall be capable of and configured to reduce flow automatically through the

*boiler system* when a boiler is shut down.

C403.4.6 Reserved.

**C403.4.7 Heating and cooling system controls for operable openings to the outdoors.** All doors from a *conditioned space* to the outdoors and all other operable openings from a *conditioned space* to the outdoors that are larger than 40 square feet (3.7 m2) when fully open shall have *automatic* controls interlocked with the heating and cooling system. The controls shall be configured to do the following within 5 minutes of opening:

1. Disable mechanical heating to the zone or reset the space heating temperature setpoint to 55°F (12.5°C) or less.
2. Disable mechanical cooling to the zone or reset the space cooling temperature setpoint to 90°F (32°C) or more. Mechani- cal cooling can remain enabled if the outdoor air temperature is below the space temperature.

Exceptions:

* 1. *Building entrances* with *automatic* closing devices.
  2. Emergency exits with an *automatic* alarm that sounds when open.
  3. Operable openings and doors serving *enclosed spaces* without a *thermostat* or heating or cooling temperature sensor.
  4. Separately zoned areas associated with the preparation of food that contain appliances that contribute to the heat- ing or cooling loads of a restaurant or similar type of occupancy.
  5. Warehouses that utilize operable openings for the function of the occupancy, where *approved* by the *code official*.
  6. The first *entrance doors* where located in the *exterior wall* and are part of a vestibule system.
  7. Operable openings into spaces served by radiant heating and cooling systems.
  8. *Alterations* where walls would have to be opened solely for the purpose of meeting this requirement and where *approved*.
  9. Doors served by air curtains meeting the requirements of Section C402.6.6.

**C403.4.8 Humidification and dehumidification controls.** Humidification and dehumidification controls shall be in accordance with this section.

**C403.4.8.1 Dehumidification.** *Humidistatic controls* shall not use mechanical cooling to reduce the humidity below the lower of a dew point of 55°F (13°C) or relative humidity of 60 percent in the coldest *zone* served by the system. Lower humidity shall be permitted where mechanical cooling is being used for temperature control.

Exceptions:

* + 1. Where approved, systems serving zones where specific humidity levels are required, such as museums and hospi- tals, and where *humidistatic controls* are capable of and configured to maintain a dead band of at least 10 percent relative humidity where no active humidification or dehumidification takes place.
    2. Systems serving *zones* where humidity levels are required to be maintained with precision of not more than ±5 percent relative humidity to comply with applicable codes or accreditation standards or as *approved* by the authority having jurisdiction.

**C403.4.8.2 Humidification.** *Humidistatic controls* shall not use fossil fuels or electricity to produce relative humidity above 30 percent in the warmest *zone* served by the system.

Exceptions:

1. Where *approved*, systems serving *zones* where specific humidity levels are required, such as museums and hospi- tals, and where *humidistatic controls* are capable of and configured to maintain a deadband of at least 10 percent relative humidity where no active humidification or dehumidification takes place.
2. Systems serving *zones* where humidity levels are required to be maintained with precision of not more than ±5 percent relative humidity to comply with applicable codes or accreditation standards or as *approved* by the authority having jurisdiction.

**C403.4.8.3 Control interlock.** Where a *zone* is served by a system or systems with both humidification and dehumidification capability, means such as limit switches, mechanical stops, or for DDC systems, software programming, shall be provided capable of and configured to prevent simultaneous operation of humidification and dehumidification equipment.

**Exception:** Systems serving *zones* where humidity levels are required to be maintained with precision of not more than ±5 percent relative humidity to comply with applicable codes or accreditation standards or as *approved* by the authority having jurisdiction.

**C403.5 Economizers.** Economizers shall comply with Sections C403.5.1 through C403.5.5.

An air or *water economizer* shall be provided for the following cooling systems:

1. Chilled water systems with a total cooling capacity, less cooling capacity provided with air economizers, as specified in Table C403.5(1).
2. Individual *fan systems* with cooling capacity greater than or equal to 54,000 Btu/h (15.8 kW) in *buildings* having other than a

*Group R* occupancy.

The total supply capacity of all fan cooling units not provided with economizers shall not exceed 20 percent of the total supply capacity of all fan cooling units in the *building* or 300,000 Btu/h (88 kW), whichever is greater.

1. Individual *fan systems* with cooling capacity greater than or equal to 270,000 Btu/h (79.1 kW) in *buildings* having a *Group R*

occupancy.

The total supply capacity of all fan cooling units not provided with economizers shall not exceed 20 percent of the total supply capacity of all fan cooling units in the *building* or 1,500,000 Btu/h (440 kW), whichever is greater.

**Exceptions:** Economizers are not required for the following systems.

* 1. Individual *fan systems* not served by chilled water for *buildings* located in Climate Zones 0A, 0B, 1A and 1B.
  2. Where more than 25 percent of the air designed to be supplied by the system is to spaces that are designed to be humid- ified above 35°F (1.7°C) dew-point temperature to satisfy process needs.
  3. Systems expected to operate less than 20 hours per week.
  4. Systems serving supermarket areas with open refrigerated casework.
  5. Where the cooling efficiency is greater than or equal to the efficiency requirements in Table C403.5(2).
  6. Systems that include a heat recovery system in accordance with Section C403.11.5.
  7. Direct-expansion fan coils or unitary equipment with a capacity less than 54,000 Btu/h (15.8 kW) and multiple stages of compressor capacity installed with a dedicated outdoor air system.

|  |  |  |
| --- | --- | --- |
| **TABLE C403.5(1)—MINIMUM CHILLED-WATER SYSTEM COOLING CAPACITY FOR DETERMINING ECONOMIZER COOLING REQUIREMENTS** | | |
| **CLIMATE ZONES (COOLING)** | **TOTAL CHILLED-WATER SYSTEM CAPACITY LESS CAPACITY OF COOLING UNITS WITH AIR ECONOMIZERS** | |
| **Local Water-Cooled Chilled-Water Systems** | **Air-Cooled Chilled-Water Systems or District Chilled-Water Systems** |
| 0A, 1A | Economizer not required | Economizer not required |
| 0B, 1B, 2A, 2B | 960,000 Btu/h | 1,250,000 Btu/h |
| 3A, 3B, 3C, 4A, 4B, 4C | 720,000 Btu/h | 940,000 Btu/h |
| 5A, 5B, 5C, 6A, 6B, 7, 8 | 1,320,000 Btu/h | 1,720,000 Btu/h |
| For SI: 1 British thermal unit per hour = 0.2931 W. | | |

|  |  |
| --- | --- |
| **TABLE C403.5(2)—EQUIPMENT EFFICIENCY PERFORMANCE EXCEPTION FOR ECONOMIZERS** | |
| **CLIMATE ZONES** | **COOLING EQUIPMENT PERFORMANCE IMPROVEMENT (EER OR IPLV)** |
| 2A, 2B | 10% efficiency improvement |
| 3A, 3B | 15% efficiency improvement |
| 4A, 4B | 20% efficiency improvement |

**C403.5.1 Integrated economizer control.** Economizer systems shall be integrated with the mechanical cooling system and be configured to provide partial cooling even where additional mechanical cooling is required to provide the remainder of the cool- ing load. Controls shall not be capable of creating a false load in the mechanical cooling systems by limiting or disabling the economizer or any other means, such as hot gas bypass, except at the lowest stage of mechanical cooling.

Units that include an *air economizer* shall comply with the following:

1. Unit controls shall have the mechanical cooling capacity control interlocked with the *air economizer* controls such that the outdoor air damper is at the 100 percent open position when mechanical cooling is on and the outdoor air damper does not begin to close to prevent coil freezing due to minimum compressor run time until the leaving air temperature is less than 45°F (7°C).
2. Direct expansion (DX) units that control 75,000 Btu/h (22 kW) or greater of rated capacity of the capacity of the mechani- cal cooling directly based on occupied space temperature shall have not fewer than two stages of mechanical cooling capacity.
3. Other DX units, including those that control space temperature by modulating the airflow to the space, shall be in accor- dance with Table C403.5.1.

|  |  |  |
| --- | --- | --- |
| **TABLE C403.5.1—DX COOLING STAGE REQUIREMENTS FOR MODULATING AIRFLOW UNITS** | | |
| **RATING CAPACITY** | **MINIMUM NUMBER OF MECHANICAL COOLING STAGES** | **MINIMUM COMPRESSOR DISPLACEMENTa** |
| ≥ 65,000 Btu/h and  < 240,000 Btu/h | 3 stages | ≤ 35% of full load |
| ≥ 240,000 Btu/h | 4 stages | ≤ 25% full load |
| For SI: 1 British thermal unit per hour = 0.2931 W.  a. For mechanical cooling stage control that does not use variable compressor displacement, the percent displacement shall be equivalent to the mechanical cooling capacity reduction evaluated at the full load rating conditions for the compressor. | | |

**C403.5.2 Economizer heating system impact.** HVAC system design and economizer controls shall be such that economizer operation does not increase *building* heating energy use during normal operation.

**Exception:** Economizers on variable air volume (VAV) systems that cause *zone* level heating to increase because of a reduction in supply air temperature.

**C403.5.3 Air economizers.** Where economizers are required by Section C403.5, air economizers shall comply with Sections C403.5.3.1 through C403.5.3.5.

**C403.5.3.1 Design capacity.** *Air economizer* systems shall be configured to modulate outdoor air and return air dampers to provide up to 100 percent of the design supply air quantity as outdoor air for cooling.

**C403.5.3.2 Control signal.** Economizer controls and dampers shall be configured to sequence the dampers with the mechani- cal cooling equipment and shall not be controlled by only mixed-air temperature.

**Exception:** The use of mixed-air temperature limit control shall be permitted for systems controlled from space temperature (such as single-*zone* systems).

**C403.5.3.3 High-limit shutoff.** Air economizers shall be configured to automatically reduce outdoor air intake to the design minimum outdoor air quantity when outdoor air intake will not reduce cooling energy usage. High-limit shutoff control types for specific climates shall be chosen from Table C403.5.3.3. High-limit shutoff control settings for these control types shall be those specified in Table C403.5.3.3.

|  |  |  |  |
| --- | --- | --- | --- |
| **TABLE C403.5.3.3—HIGH-LIMIT SHUTOFF CONTROL SETTING FOR AIR ECONOMIZERSb** | | | |
| **DEVICE TYPE** | **CLIMATE ZONE** | **REQUIRED HIGH LIMIT (ECONOMIZER OFF WHEN):** | |
| **Equation** | **Description** |
| Fixed dry bulb | 0B, 1B, 2B, 3B, 3C, 4B, 4C,  5B, 5C, 6B, 7, 8 | *TOA* > 75°F | Outdoor air temperature exceeds 75°F |
| 5A, 6A | *TOA* > 70°F | Outdoor air temperature exceeds 70°F |
| 0A, 1A, 2A, 3A, 4A | *TOA* > 65°F | Outdoor air temperature exceeds 65°F |
| Differential dry bulb | 0B, 1B, 2B, 3B, 3C, 4B, 4C,  5A, 5B, 5C, 6A, 6B, 7, 8 | *TOA > TRA* | Outdoor air temperature exceeds return air temperature |
| Fixed enthalpy with fixed dry-bulb temperatures | All | *hOA* > 28 Btu/lba or *TOA* > 75°F | Outdoor air enthalpy exceeds 28 Btu/lb of dry aira or |
| Outdoor air temperature exceeds 75°F |
| Differential enthalpy with fixed dry-bulb temperature | All | *hOA* > *hRA* or *TOA* > 75°F | Outdoor air enthalpy exceeds return air enthalpy or |
| Outdoor air temperature exceeds 75°F |
| For SI: °C = (°F – 32)/1.8, 1 Btu/lb = 2.33 kJ/kg.   1. At altitudes substantially different than sea level, the fixed enthalpy limit shall be set to the enthalpy value at 75°F and 50 percent relative humidity. As an example, at approximately 6,000 feet elevation, the fixed enthalpy limit is approximately 30.7 Btu/lb. 2. Devices with selectable setpoints shall be capable of being set to within 2°F and 2 Btu/lb of the setpoint listed. | | | |

**C403.5.3.4 Relief of excess outdoor air.** Systems shall provide one of the following means to relieve excess outdoor air during

*air economizer* operation to prevent overpressurizing the *building*.

* 1. Return or relief fan(s) meeting the requirements of Section C403.11.1.
  2. A barometric or motorized damper relief path with a total pressure drop at a design relief airflow rate less than 0.10 inches water column (25 Pa) from the occupied space to the outdoors. Design relief airflow rate shall be the design supply airflow rate minus any continuous exhaust flows, such as toilet exhaust fans, whose makeup is provided by the economizer system.

The relief air outlet shall be located to avoid recirculation into the *building*.

**C403.5.3.5 Economizer dampers.** Return, exhaust/relief and outdoor air dampers used in economizers shall comply with Section C403.7.7.

**C403.5.4 Water-side economizers.** Where economizers are required by Section C403.5, water-side economizers shall comply with Sections C403.5.4.1 and C403.5.4.2.

**C403.5.4.1 Design capacity.** *Water economizer* systems shall be configured to cool supply air by indirect evaporation and providing up to 100 percent of the expected system cooling load at outdoor air temperatures of not greater than 50°F (10°C) dry bulb/45°F (7°C) wet bulb.

Exceptions:

* + 1. Systems primarily serving *computer rooms* in which 100 percent of the expected system cooling load at 40°F (4°C) dry bulb/35°F (1.7°C) wet bulb is met with evaporative water economizers.
    2. Systems primarily serving *computer rooms* with dry cooler water economizers that satisfy 100 percent of the expected system cooling load at 35°F (1.7°C) dry bulb.
    3. Systems where dehumidification requirements cannot be met using outdoor air temperatures of 50°F (10°C) dry bulb/45°F (7°C) wet bulb and where 100 percent of the expected system cooling load at 45°F (7°C) dry bulb/40°F (4°C) wet bulb is met with evaporative water economizers.

**C403.5.4.2 Maximum pressure drop.** Precooling coils and water-to-water heat exchangers used as part of a *water economizer* system shall either have a water-side pressure drop of less than 15 feet (45 kPa) of water or a secondary loop shall be created so that the coil or heat exchanger pressure drop is not seen by the circulating pumps when the system is in the normal cooling (noneconomizer) mode.

**C403.5.5 Economizer fault detection and diagnostics.** Air-cooled unitary direct-expansion units listed in the tables in Section C403.3.2 and variable refrigerant flow (VRF) units that are equipped with an economizer in accordance with Sections C403.5 through C403.5.4 shall include a fault detection and diagnostics system complying with the following:

1. The following temperature sensors shall be permanently installed to monitor system operation:
   1. Outside air.
   2. Supply air.
   3. Return air.
2. Temperature sensors shall have an accuracy of ±2°F (1.1°C) over the range of 40°F to 80°F (4°C to 26.7°C).
3. Refrigerant pressure sensors, where used, shall have an accuracy of ±3 percent of full scale.
4. The unit controller shall be configured to provide system status by indicating the following:
   1. Free cooling available.
   2. Economizer enabled.
   3. Compressor enabled.
   4. Heating enabled.
   5. Mixed air low limit cycle active.
   6. The current value of each sensor.
5. The unit controller shall be capable of manually initiating each operating mode so that the operation of compressors, economizers, fans and the heating system can be independently tested and verified.
6. The unit shall be configured to report faults to a fault management application available for *access* by day-to-day oper- ating or service personnel, or annunciated locally on *zone thermostats*.
7. The fault detection and diagnostics system shall be configured to detect the following faults:
   1. Air temperature sensor failure/fault.
   2. Not economizing when the unit should be economizing.
   3. Economizing when the unit should not be economizing.
   4. Damper not modulating.
   5. Excess outdoor air.

**C403.6 Requirements for mechanical systems serving multiple zones.** Sections C403.6.1 through C403.6.9 shall apply to mechan- ical systems serving multiple *zones*.

**C403.6.1 Variable air volume and multiple-zone systems.** Supply air systems serving multiple *zones* shall be variable air volume (VAV) systems that have *zone* controls configured to reduce the volume of air that is reheated, recooled or mixed in each *zone* to one of the following:

1. Thirty percent of the *zone* design peak supply for systems with *direct digital control* (DDC).
2. Systems with DDC where all of the following apply:
   1. The airflow rate in the deadband between heating and cooling does not exceed the highest of the allowed rates under Items 3, 4, 5 or 6 of this section.
   2. The first stage of heating modulates the *zone* supply air temperature setpoint up to a maximum setpoint while the airflow is maintained at the deadband flow rate.
   3. The second stage of heating modulates the airflow rate from the deadband flow rate up to the heating maxi- mum flow rate that is less than 50 percent of the *zone* design peak supply rate.
3. The outdoor airflow rate required to meet the minimum *ventilation* requirements of Chapter 4 of the *International Mechanical Code*.
4. The minimum primary airflow rate required to meet the Simplified Procedure *ventilation* requirements of ASHRAE 62.1 for the zone and is permitted to be the average airflow rate as allowed by ASHRAE 62.1.
5. Any higher rate that can be demonstrated to reduce overall system annual energy use by offsetting reheat/recool energy losses through a reduction in outdoor air intake for the system as *approved* by the *code official*.
6. The airflow rate required to comply with applicable codes or accreditation standards such as pressure relationships or minimum air change rates.

**Exception:** The following individual *zones* or entire air distribution systems are exempted from the requirement for VAV control:

1. *Zones* or supply air systems where not less than 75 percent of the energy for reheating or for providing warm air in mixing systems is provided from a site-recovered, including condenser heat, or site-solar energy source.
2. Systems that prevent reheating, recooling, mixing or simultaneous supply of air that has been previously cooled, either mechanically or through the use of economizer systems, and air that has been previously mechanically heated.

**C403.6.2 Single-duct VAV systems, terminal devices.** Single-duct VAV systems shall use terminal devices capable of and config- ured to reduce the supply of primary supply air before reheating or recooling takes place.

**C403.6.3 Dual-duct and mixing VAV systems, terminal devices.** Systems that have one warm air *duct* and one cool air *duct* shall use terminal devices that are configured to reduce the flow from one *duct* to a minimum before mixing of air from the other *duct* takes place.

**C403.6.4 Single-fan dual-duct and mixing VAV systems, economizers.** Individual dual-duct or mixing heating and cooling systems with a single fan and with total capacities greater than 90,000 Btu/h [(26.4 kW) 7.5 tons] shall not be equipped with air economizers.

**C403.6.5 Supply-air temperature reset controls.** Multiple-zone HVAC systems shall include controls that are capable of and configured to automatically reset the supply-air temperature in response to representative *building* loads, or to outdoor air temperature. The controls shall be configured to reset the supply air temperature not less than 25 percent of the difference between the design supply-air temperature and the design room air temperature. Controls that adjust the reset based on *zone* humidity are allowed in Climate Zones 0B, 1B, 2B, 3B, 3C and 4 through 8. HVAC *zones* that are expected to experience relatively constant loads shall have maximum airflow designed to accommodate the fully reset supply-air temperature.

Exceptions:

* 1. Systems that prevent reheating, recooling or mixing of heated and cooled supply air.
  2. Seventy-five percent of the energy for reheating is from site-recovered or site-solar energy sources.
  3. Systems in Climate Zones 0A, 1A and 3A with less than 3,000 cfm (1500 L/s) of design outside air.
  4. Systems in Climate Zone 2A with less than 10,000 cfm (5000 L/s) of design outside air.
  5. Systems in Climate Zones 0A, 1A, 2A and 3A with not less than 80 percent outside air and employing exhaust air energy recovery complying with Section C403.7.4.

**C403.6.5.1 Dehumidification control interaction.** In Climate Zones 0A, 1A, 2A and 3A, the system design shall allow supply- air temperature reset while dehumidification is provided. When dehumidification control is active, air economizers shall be locked out.

**C403.6.6 Multiple-zone VAV system ventilation optimization control.** Multiple-zone VAV systems with *direct digital control* of individual *zone* boxes reporting to a central control panel shall have *automatic* controls configured to reduce outdoor air intake flow below design rates in response to changes in system *ventilation* efficiency ( *E v* ) as defined by the *International Mechanical Code*.

Exceptions:

1. VAV systems with zonal transfer fans that recirculate air from other *zones* without directly mixing it with outdoor air, dual-duct dual-fan VAV systems, and VAV systems with fan-powered terminal units.
2. Systems where total design exhaust airflow is more than 70 percent of total design outdoor air intake flow requirements.

**C403.6.7 Parallel-flow fan-powered VAV air terminal control.** Parallel-flow fan-powered VAV air terminals shall have *automatic*

controls configured to:

1. Turn off the terminal fan except when space heating is required or where required for *ventilation*.
2. Turn on the terminal fan as the first stage of heating before the heating coil is activated.
3. During heating for warmup or setback temperature control, either:
   1. Operate the terminal fan and heating coil without primary air.
   2. Reverse the terminal damper logic and provide heating from the central air handler by primary air.

**C403.6.8 Setpoints for direct digital control.** For systems with *direct digital control* of individual *zones* reporting to the central control panel, the static pressure setpoint shall be reset based on the *zone* requiring the most pressure. In such case, the setpoint is reset lower until one *zone* damper is nearly wide open. The *direct digital controls* shall be capable of monitoring zone damper positions or shall have an alternative method of indicating the need for static pressure that is configured to provide all of the following:

1. *Automatic* detection of any *zone* that excessively drives the reset logic.
2. Generation of an alarm to the system operational location.
3. Allowance for an operator to readily remove one or more *zones* from the reset algorithm.

**C403.6.9 Static pressure sensor location.** Static pressure sensors used to control VAV fans shall be located such that the control- ler setpoint is not greater than 1.2 inches w.c. (299 Pa). Where this results in one or more sensors being located downstream of major duct splits, not less than one sensor shall be located on each major branch to ensure that static pressure can be maintained in each branch.

**C403.7 Ventilation and exhaust systems.** In addition to other requirements of Section C403 applicable to the provision of *ventila- tion* air or the exhaust of air, *ventilation* and exhaust systems shall be in accordance with Sections C403.7.1 through C403.7.9.

**C403.7.1 Demand control ventilation.** Demand control ventilation (DCV) shall be provided for the following:

1. Spaces with *ventilation* provided by single-zone systems where an air-side economizer is provided in accordance with Section C403.5.
2. Spaces larger than 250 square feet (23 m2) in Climate Zones 5A, 6, 7, and 8 and spaces larger than 500 square feet (46.5 m2) in other *climate zones* that have a design occupant load of 15 people or greater per 1,000 square feet (93 m2) of floor area, as established in Table 403.3.1.1 of the *International Mechanical Code*, and are served by systems with one or more of the following:
   1. An air-side economizer.
   2. *Automatic* modulating control of the outdoor air damper.
   3. A design outdoor airflow greater than 3,000 cfm (1416 L/s).

Exceptions:

1. Spaces served by systems with energy recovery in accordance with Section C403.7.4.2 and that have a floor area less than:
   1. 6,000 square feet (557 m2) in Climate Zone 3C.
   2. 2,000 square feet (186 m2) in Climate Zones 1A, 3B and 4B.
   3. 1,000 square feet (93 m2) in Climate Zones 2A, 2B, 3A, 4A, 4C, 5 and 6.
   4. 400 square feet (37 m2) in Climate Zones 7 and 8.
2. Multiple-zone systems without *direct digital control* of individual zones communicating with a central control panel.
3. Spaces served by multiple-zone systems with a design outdoor airflow less than 750 cfm (354 L/s).
4. Spaces where more than 75 percent of the space design outdoor airflow is required for makeup air that is exhausted from the space or transfer air that is required for makeup air that is exhausted from other spaces.
5. Spaces with one of the following occupancy classifications as defined in Table 403.3.1.1 of the *International Mechani- cal Code*: correctional cells, education laboratories, barber, beauty and nail salons, and bowling alley seating areas.
6. Spaces where the *registered design professional* demonstrates an engineered ventilation system design that:
   1. Prevents the maximum concentration of contaminants from being more than that obtainable by the required rate of outdoor air *ventilation*.
   2. Allows the required minimum design rate of outdoor air to be reduced by not less than 15 percent.

**C403.7.2 Parking garage ventilation controls.** Ventilation systems employed in enclosed parking garages shall comply with Section 404.1 of the *International Mechanical Code* and the following:

1. Separate ventilation systems and control systems shall be provided for each *parking garage section*.
2. Control systems for each *parking garage section* shall be capable of and configured to reduce fan airflow to not less than

0.05 cfm per square foot [0.00025 m3 /(s × m2)] of the floor area served and not more than 20 percent of the design capacity.

1. The ventilation system for each *parking garage section* shall have controls and devices that result in fan motor demand of not more than 30 percent of design wattage at 50 percent of the design airflow.

**Exception:** Garage ventilation systems serving a single *parking garage section* having a total ventilation system motor *name- plate horsepower* (ventilation system motor nameplate kilowatt) not exceeding 5 hp (3.7 kW) at *fan system design conditions* and where the *parking garage section* has no mechanical cooling or mechanical heating.

Nothing in this section shall be construed to require more than one *parking garage section* in any parking structure.

**C403.7.3 Ventilation air heating control.** Units that provide *ventilation* air to multiple *zones* and operate in conjunction with *zone* heating and cooling systems shall not use heating or heat recovery to warm supply air to a temperature greater than 60°F (16°C) when representative *building* loads or outdoor air temperatures indicate that the majority of *zones* require cooling.

**Exception:** Units that heat the airstream using only *series energy recovery* when representative *building* loads or outdoor air temperature indicates that the majority of *zones* require cooling in Climate Zones 0A, 1A, 2A, 3A and 4A.

**C403.7.4 Energy recovery systems.** Energy recovery ventilation systems shall be provided as specified in either Section C403.7.4.1 or C403.7.4.2, as applicable.

**C403.7.4.1 Nontransient dwelling units.** Nontransient dwelling units shall be provided with outdoor air energy recovery ventilation systems complying with not less than one of the following:

* 1. The system shall have an enthalpy recovery ratio of not less than 50 percent at cooling design condition and not less than 60 percent at heating design condition.
  2. The system shall have a sensible recovery efficiency (SRE) that is not less than 65 percent at 32°F (0°C) and in Climate Zones 0A, 1A, 2A and 3A shall have a net moisture transfer (NMT) that is not less than 40 percent at 95°F (35°C). SRE and NMT shall be determined from a listed value or from interpolation of listed values at an airflow not less than the design airflow, based on testing in accordance with CAN/CSA C439.

Exceptions:

* + 1. Nontransient dwelling units in Climate Zone 3C.
    2. Nontransient dwelling units with not more than 500 square feet (46 m2) of *conditioned floor area* in Climate Zones 0, 1, 2, 3, 4C and 5C.
    3. *Enthalpy recovery ratio* requirements at heating design condition in Climate Zones 0, 1 and 2.
    4. *Enthalpy recovery ratio* requirements at cooling design condition in Climate Zones 4, 5, 6, 7 and 8.

**C403.7.4.2 Spaces other than nontransient dwelling units.** Where the supply airflow rate of a *fan system* serving a space other than a nontransient dwelling unit exceeds the values specified in Tables C403.7.4.2(1) and C403.7.4.2(2), the system shall include an energy recovery system. The energy recovery system shall provide an *enthalpy recovery ratio* of not less than 50 percent at design conditions. Where an *air economizer* is required, the energy recovery system shall include a bypass or controls that permit operation of the economizer as required by Section C403.5.

**Exception:** An *energy recovery ventilation system* shall not be required in any of the following conditions:

* + - 1. Where energy recovery systems are prohibited by the *International Mechanical Code*.
      2. Laboratory fume hood systems that include not fewer than one of the following features:
         1. Variable-air-volume hood exhaust and room supply systems configured to reduce exhaust and makeup air volume to 50 percent or less of design values.
         2. Direct makeup (auxiliary) air supply equal to or greater than 75 percent of the exhaust rate, heated not warmer than 2°F (1.1°C) above room setpoint, cooled to not cooler than 3°F (1.7°C) below room setpoint, with no humidification added, and no simultaneous heating and cooling used for dehumidification control.
      3. Systems serving spaces that are heated to less than 60°F (15.5°C) and that are not cooled.
      4. Heating energy recovery where more than 60 percent of the outdoor heating energy is provided from site-recov- ered or site-solar energy in Climate Zones 5 through 8.
      5. *Enthalpy recovery ratio* requirements at heating design condition in Climate Zones 0, 1 and 2.
      6. *Enthalpy recovery ratio* requirements at cooling design condition in Climate Zones 3C, 4C, 5B, 5C, 6B, 7 and 8.
      7. Systems in Climate Zones 0 through 4 requiring dehumidification that employ series energy recovery land have a minimum SERR of 0.40.
      8. Where the largest source of air exhausted at a single location at the *building* exterior is less than 75 percent of the design outdoor airflow rate.
      9. Systems expected to operate less than 20 hours per week at the *outdoor air* percentage covered by Table C403.7.4.2(1).
      10. Systems exhausting toxic, flammable, paint or corrosive fumes or dust.
      11. Commercial kitchen hoods used for collecting and removing grease vapors and smoke.

|  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE C403.7.4.2(1)—ENERGY RECOVERY REQUIREMENT (Ventilation systems operating less than 8,000 hours per year)** | | | | | | | | |
| **CLIMATE ZONE** | **PERCENT (%) OUTDOOR AIR AT FULL DESIGN AIRFLOW RATE** | | | | | | | |
| **≥ 10% and**  **< 20%** | **≥ 20% and**  **< 30%** | **≥ 30% and**  **< 40%** | **≥ 40% and**  **< 50%** | **≥ 50% and**  **< 60%** | **≥ 60% and**  **< 70%** | **≥ 70% and**  **< 80%** | **≥ 80%** |
| **Design Supply Fan Airflow Rate (cfm)** | | | | | | | |
| 3B, 3C, 4B, 4C, 5B | NR | NR | NR | NR | NR | NR | NR | NR |
| 0B, 1B, 2B, 5C | NR | NR | NR | NR | ≥ 26,000 | ≥ 12,000 | ≥ 5,000 | ≥ 4,000 |
| 6B | ≥ 28,000 | ≥ 26,500 | ≥ 11,000 | ≥ 5,500 | ≥ 4,500 | ≥ 3,500 | ≥ 2,500 | ≥ 1,500 |
| 0A, 1A, 2A, 3A, 4A, 5A, 6A | ≥ 26,000 | ≥ 16,000 | ≥ 5,500 | ≥ 4,500 | ≥ 3,500 | ≥ 2,000 | ≥ 1,000 | > 120 |
| 7, 8 | ≥ 4,500 | ≥ 4,000 | ≥ 2,500 | ≥ 1,000 | > 140 | > 120 | > 100 | > 80 |
| For SI: 1 cfm = 0.4719 L/s. NR = Not Required. | | | | | | | | |

|  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE C403.7.4.2(2)—ENERGY RECOVERY REQUIREMENT (Ventilation systems operating not less than 8,000 hours per year)** | | | | | | | | |
| **CLIMATE ZONE** | **PERCENT (%) OUTDOOR AIR AT FULL DESIGN AIRFLOW RATE** | | | | | | | |
| **≥ 10% and**  **< 20%** | **≥ 20% and**  **< 30%** | **≥ 30% and**  **< 40%** | **≥ 40% and**  **< 50%** | **≥ 50% and**  **< 60%** | **≥ 60% and**  **< 70%** | **≥ 70% and**  **< 80%** | **≥ 80%** |
| **Design Supply Fan Airflow Rate (cfm)** | | | | | | | |
| 3C | NR | NR | NR | NR | NR | NR | NR | NR |
| 0B, 1B, 2B, 3B, 4C, 5C | NR | ≥ 19,500 | ≥ 9,000 | ≥ 5,000 | ≥ 4,000 | ≥ 3,000 | ≥ 1,500 | ≥ 120 |
| 0A, 1A, 2A, 3A, 4B, 5B | ≥ 2,500 | ≥ 2,000 | ≥ 1,000 | ≥ 500 | ≥ 140 | ≥ 120 | ≥ 100 | ≥ 80 |
| 4A, 5A, 6A, 6B, 7, 8 | ≥ 200 | ≥ 130 | ≥ 100 | ≥ 80 | ≥ 70 | ≥ 60 | ≥ 50 | ≥ 40 |
| For SI: 1 cfm = 0.4719 L/s. NR = Not Required. | | | | | | | | |

**C403.7.5 Kitchen exhaust systems.** Replacement air introduced directly into the exhaust hood cavity shall not be greater than 10 percent of the hood exhaust airflow rate. Conditioned supply air delivered to any space shall not exceed the greater of the following:

1. The ventilation rate required to meet the space heating or cooling load.
2. The hood exhaust flow minus the available transfer air from adjacent space where available transfer air is considered to be that portion of outdoor *ventilation* air not required to satisfy other exhaust needs, such as restrooms, and not required to maintain pressurization of adjacent spaces.

Kitchen exhaust hood systems serving Type I exhaust hoods shall be provided with *demand control kitchen ventilation* (DCKV) controls where a kitchen or kitchen/dining facility has a total Type I kitchen hood exhaust airflow rate greater than 5,000 cubic feet per minute (2360 L/s). DCKV systems shall be configured to provide a minimum of 50 percent reduction in exhaust and replacement air system airflow rates. Systems shall include controls necessary to modulate exhaust and replacement air system airflows in response to appliance operation and to maintain full capture and containment of smoke, effluent and combustion products during cooking and idle operation. Each hood shall be a factory-built commercial exhaust hood *listed* by a nationally recognized testing laboratory and shall have a maximum exhaust rate as specified in Table C403.7.5.

Where a single hood, or hood section, is installed over appliances with different duty ratings, the maximum allowable flow rate for the hood or hood section shall be based on the requirements for the highest appliance duty rating under the hood or hood section.

Exceptions:

* 1. UL 710 listed exhaust hoods that have a design maximum exhaust flow rate not greater than 250 cubic feet per minute (118 L/s) per linear foot (305 mm) of hood that serve kitchen or kitchen/dining facilities with a total kitchen hood exhaust airflow rate less than 5,000 cfm (2360 L/s).
  2. Where allowed by the *International Mechanical Code*, an *energy recovery ventilation system* is installed on the kitchen exhaust with a sensible heat recovery effectiveness of not less than 40 percent on not less than 50 percent of the total exhaust hood airflow.

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **TABLE C403.7.5—MAXIMUM NET EXHAUST FLOW RATE, CFM PER LINEAR FOOT OF HOOD LENGTH** | | | | |
| **TYPE OF HOOD** | **LIGHT-DUTY EQUIPMENT** | **MEDIUM-DUTY EQUIPMENT** | **HEAVY-DUTY EQUIPMENT** | **EXTRA-HEAVY-DUTY EQUIPMENT** |
| Wall-mounted canopy | 140 | 210 | 280 | 385 |
| Single island | 280 | 350 | 420 | 490 |
| Double island (per side) | 175 | 210 | 280 | 385 |
| Eyebrow | 175 | 175 | NA | NA |
| Backshelf/Pass-over | 210 | 210 | 280 | NA |
| For SI: 1 cfm = 0.4719 L/s; 1 foot = 304.8 mm. NA = Not Allowed. | | | | |

**C403.7.6 Automatic control of HVAC systems serving guestrooms.** In Group R-1 *buildings* containing more than 50 guestrooms, each guestroom shall be provided with controls complying with the provisions of Sections C403.7.6.1 and C403.7.6.2.

**C403.7.6.1 Temperature setpoint controls.** Controls shall be provided on each HVAC system that are capable of and config- ured with three modes of temperature control.

1. When the guestroom is rented but unoccupied, the controls shall automatically raise the cooling setpoint and lower the heating setpoint by not less than 4°F (2°C) from the occupant setpoint within 30 minutes after the occupants have left the guestroom.
2. When the guestroom is unrented and unoccupied, the controls shall automatically raise the cooling setpoint to not lower than 80°F (27°C) and lower the heating setpoint to not higher than 60°F (16°C). Unrented and unoccupied gues- troom mode shall be initiated within 16 hours of the guestroom being continuously occupied or where a *networked guestroom control system* indicates that the guestroom is unrented and the guestroom is unoccupied for more than 20 minutes. A *networked guestroom control system* that is capable of returning the *thermostat* setpoints to default occupied setpoints 60 minutes prior to the time a guestroom is scheduled to be occupied is not precluded by this section. Cooling that is capable of limiting relative humidity with a setpoint not lower than 65 percent relative humid- ity during unoccupied periods is not precluded by this section.
3. When the guestroom is occupied, HVAC setpoints shall return to their occupied setpoints once occupancy is sensed.

**C403.7.6.2 Ventilation controls.** Controls shall be provided on each HVAC system that are capable of and configured to auto- matically turn off the *ventilation* and exhaust fans within 20 minutes of the occupants leaving the guestroom, or *isolation*

*devices* shall be provided to each guestroom that are capable of automatically shutting off the supply of outdoor air to and exhaust air from the guestroom.

**Exception:** Guestroom ventilation systems are not precluded from having an *automatic* daily pre-occupancy purge cycle that provides daily outdoor air *ventilation* during unrented periods at the design ventilation rate for 60 minutes, or at a rate and duration equivalent to one air change.

**C403.7.7 Shutoff dampers.** Outdoor air intake and exhaust openings and stairway and shaft vents shall be provided with Class I motorized dampers. The dampers shall have an *air leakage* rate not greater than 4 cfm/ft 2(20.3 L/s × m2) of damper surface area at 1.0 inch water gauge (249 Pa) and shall be *labeled* by an *approved agency* when tested in accordance with AMCA 500D for such purpose.

Outdoor air intake and exhaust dampers shall be installed with *automatic* controls configured to close when the systems or spaces served are not in use or during unoccupied period warm-up and setback operation, unless the systems served require outdoor or exhaust air in accordance with the *International Mechanical Code* or the dampers are opened to provide intentional economizer cooling.

Stairway and elevator shaft vent dampers shall be installed with *automatic* controls configured to open upon the activation of any fire alarm initiating device of the *building’s* fire alarm system, the interruption of power to the damper, or by thermostatic control systems.

**Exception:** Nonmotorized gravity dampers shall be an alternative to motorized dampers for exhaust and relief openings as follows:

* 1. In *buildings* less than three stories in height above grade plane.
  2. In *buildings* of any height located in Climate Zones 0, 1, 2 or 3.
  3. Where the design exhaust capacity is not greater than 300 cfm (142 L/s).

Nonmotorized gravity dampers shall have an *air leakage* rate not greater than 20 cfm/ft2(101.6 L/s × m2) where not less than 24 inches (610 mm) in either dimension and 40 cfm/ft2(203.2 L/s × m2) where less than 24 inches (610 mm) in either dimension. The rate of *air leakage* shall be determined at 1.0 inch water gauge (249 Pa) when tested in accordance with AMCA 500D for such purpose. The dampers shall be *labeled* by an *approved agency*.

**C403.7.8 Occupied standby controls.** The following spaces shall be equipped with occupied standby controls in accordance with Section C403.7.8.1 for each ventilation zone:

1. Postsecondary classrooms, lecture rooms and training rooms.
2. Conference/meeting/multipurpose rooms.
3. Lounges/breakrooms.
4. Enclosed offices.
5. Open-plan office areas.
6. Corridors.

**Exception:** Zones that are part of a multiple-zone system without automatic zone flow control dampers.

**C403.7.8.1 Occupied-standby zone controls.** Within 5 minutes of all spaces in that *zone* entering *occupied-standby mode*, the

*zone* control shall operate as follows:

* 1. The active heating setpoint shall be set back by not less than 1°F (0.55°C).
  2. The active cooling setpoint shall be set up by not less than 1°F (0.55°C).
  3. All airflow supplied to the *zone* shall be shut off whenever the space temperature is between the active heating and cooling setpoints.
  4. Multiple-zone systems shall comply with Section C403.7.8.1.1.

**C403.7.8.1.1 Multiple-zone system controls.** Multiple-zone systems required to automatically reset the effective minimum outdoor air setpoint, per Section C403.6.6, shall reset the effective minimum outdoor air setpoint based on a *zone* outdoor air requirement of zero for all *zones* in *occupied-standby mode*. Sequences of operation for system outside air reset shall comply with an *approved* method.

**C403.7.9 Dwelling unit ventilation system.** A fan that is the air mover for a heating or cooling system that serves an individual

*dwelling unit* shall not be used to provide outdoor air.

**Exception:** Where the fan efficacy is not less than 1.2 cubic feet per minute (0.56 L/s) of outdoor airflow per watt when there is no demand for heating or cooling.

**C403.8 Fans and fan controls.** Fans in HVAC systems shall comply with Sections C403.8.1 through C403.8.6.1.

**C403.8.1 Allowable fan horsepower.** Where the summed fan system motor *nameplate horsepower* on an HVAC *fan system* is greater than 5 hp (3.7 kW) at *fan system design conditions*, it shall not be greater than the allowable total *fan system motor name- plate hp* (Option 1) or *fan system bhp* (Option 2), as specified in Table C403.8.1(1). Such summed HVAC fan system motor *nameplate horsepower* shall include supply fans, exhaust fans, return or relief fans, and fan-powered terminal units associated

with systems providing heating or cooling capability. Single-zone variable air volume systems shall comply with the constant volume fan power limitation.

Exceptions:

1. Hospital, vivarium and laboratory systems that utilize flow control devices on exhaust or return to maintain space pressure relationships necessary for occupant health and safety or environmental control shall be permitted to use variable volume fan power limitation.
2. Individual exhaust fans with motor *nameplate horsepower* of 1 hp (0.746 kW) or less are exempt from the allowable fan horsepower requirement.

|  |  |  |  |
| --- | --- | --- | --- |
| **TABLE C403.8.1(1)—FAN POWER LIMITATION** | | | |
|  | **LIMIT** | **CONSTANT VOLUME** | **VARIABLE VOLUME** |
| Option 1: Fan system motor nameplate hp | Allowable nameplate motor hp | hp ≤ CFMS × 0.0011 | hp ≤ CFMS × 0.0015 |
| Option 2: Fan system bhp | Allowable fan system bhp | bhp ≤ CFMS × 0.00094 + *A* | bhp ≤ CFMS × 0.0013 + *A* |
| For SI: 1 bhp = 735.5 W, 1 hp = 745.5 W, 1 cfm = 0.4719 L/s.  where:  CFMS = The maximum design supply airflow rate to conditioned spaces served by the system in cubic feet per minute. hp = The maximum combined motor nameplate horsepower.  bhp = The maximum combined fan brake horsepower.  *A* = Sum of [*PD* × CFMD / 4131].  where:  *PD* = Each applicable pressure drop adjustment from Table C403.8.1(2) in. w.c.  CFMD = The design airflow through each applicable device from Table C403.8.1(2) in cubic feet per minute. | | | |

|  |  |
| --- | --- |
| **TABLE C403.8.1(2)—FAN POWER LIMITATION PRESSURE DROP ADJUSTMENT** | |
| **DEVICE** | **ADJUSTMENT** |
| **Credits** | |
| Return air or exhaust systems required by code or accreditation stan- dards to be fully ducted, or systems required to maintain air pressure differentials between adjacent rooms | 0.5 inch w.c. (2.15 inches w.c. for laboratory and vivarium systems) |
| Return and exhaust airflow control devices | 0.5 inch w.c. |
| Exhaust filters, scrubbers or other exhaust treatment | The pressure drop of device calculated at fan system design condition |
| Particulate filtration credit: MERV 9 thru 12 | 0.5 inch w.c. |
| Particulate filtration credit: MERV 13 thru 15 | 0.9 inch w.c. |
| Particulate filtration credit: MERV 16 and greater and electronically enhanced filters | Pressure drop calculated at 2 times the clean filter pressure drop at fan system design condition. |
| Carbon and other gas-phase air cleaners | Clean filter pressure drop at fan system design condition. |
| Biosafety cabinet | Pressure drop of device at fan system design condition. |
| Energy recovery device, other than coil runaround loop | For each airstream, (2.2 × energy recovery effectiveness - 0.5) inch w.c. |
| Coil runaround loop | 0.6 inch w.c. for each airstream. |
| Evaporative humidifier/cooler in series with another cooling coil | Pressure drop of device at fan system design conditions. |
| Sound attenuation section (fans serving spaces with design back- ground noise goals below NC35) | 0.15 inch w.c. |
| Exhaust system serving fume hoods | 0.35 inch w.c. |
| Laboratory and vivarium exhaust systems in high-rise buildings | 0.25 inch w.c./100 feet of vertical duct exceeding 75 feet. |
| **Deductions** | |
| Systems without central cooling device | - 0.6 inch w.c. |
| Systems without central heating device | - 0.3 inch w.c. |
| Systems with central electric resistance heat | - 0.2 inch w.c. |
| For SI: 1 inch w.c. = 249 Pa, 1 inch = 25.4 mm, 1 foot = 304.8 mm.  w.c. = Water Column, NC = Noise Criterion. | |

**C403.8.2 Motor nameplate horsepower.** For each fan, the *fan brake horsepower* (bhp) shall be indicated on the *construction documents* and the selected motor shall be not larger than the first available motor size greater than the following:

* 1. For fans less than 6 bhp (4476 W), 1.5 times the *fan brake horsepower*.
  2. For fans 6 bhp (4476 W) and larger, 1.3 times the *fan brake horsepower*.

Exceptions:

* + 1. Fans equipped with electronic speed control devices to vary the fan airflow as a function of load.
    2. Fans with a *fan nameplate electrical input power* of less than 0.89 kW.
    3. Systems complying with Section C403.8.1 *fan system motor nameplate hp* (Option 1).
    4. Fans with motor *nameplate horsepower* less than 1 hp (746 W).

**C403.8.3 Fan efficiency.** Each fan and *fan array* shall have a *fan energy index* (FEI) of not less than 1.00 at the design point of oper- ation, as determined in accordance with AMCA 208 by an *approved* independent testing laboratory and *labeled* by the manufacturer. Each fan and *fan array* used for a variable-air-volume system shall have an FEI of not less than 0.95 at the design point of operation, as determined in accordance with AMCA 208 by an *approved* independent testing laboratory and *labeled* by the manufacturer. The FEI for fan arrays shall be calculated in accordance with AMCA 208 Annex C.

**Exceptions:** The following fans are not required to have a *fan energy index*:

1. Fans that are not *embedded fans* with motor *nameplate horsepower* of less than 1.0 hp (0.75 kW) or with a nameplate electrical input power of less than 0.89 kW.
2. *Embedded fans* that have a motor *nameplate horsepower* of 5 hp (3.7 kW) or less, or with a *fan system electrical input power* of 4.1 kW or less.
3. Multiple fans operated in series or parallel as the functional equivalent of a single fan that have a combined motor

*nameplate horsepower* of 5 hp (3.7 kW) or less or with a *fan system electrical input power* of 4.1 kW or less.

1. Fans that are part of equipment covered in Section C403.3.2.
2. Fans included in an equipment package certified by an *approved agency* for air or energy performance.
3. Ceiling fans, which are defined as nonportable devices suspended from a ceiling or overhead structure for circulating air via the rotation of the blades.
4. Fans used for moving gases at temperatures above 482°F (250°C).
5. Fans used for operation in explosive atmospheres.
6. Reversible fans used for tunnel ventilation.
7. Fans that are intended to operate only during emergency conditions.
8. Fans outside the scope of AMCA 208.

**C403.8.4 Fractional hp fan motors.** Motors for fans that are not less than 1/12 hp (0.062 kW) and are less than 1 hp (0.746 kW) shall be electronically commutated motors or shall have a minimum motor efficiency of 70 percent, rated in accordance with DOE 10 CFR 431. These motors shall have the means to adjust motor speed for either balancing or remote control. The use of belt-driven fans to sheave adjustments for airflow balancing instead of a varying motor speed shall be permitted.

**Exceptions:** The following motors are not required to comply with this section

1. Motors in the airstream within fan coils and terminal units that only provide heating to the space served.
2. Motors in space-conditioning equipment that comply with Section C403.3.2 or Sections C403.8.1. through C403.8.3.
3. Motors that comply with Section C405.8.

**C403.8.5 Low-capacity ventilation fans.** Mechanical ventilation system fans with motors less than 1/12 hp (0.062 kW) in capacity shall meet the efficacy requirements of Table C403.8.5 at one or more rating points. Airflow shall be tested in accordance with the test procedure referenced in Table C403.8.5 and *listed*. The airflow shall be reported in the product listing or on the label. Fan effi- cacy shall be reported in the product listing or shall be derived from the input power and airflow values reported in the product listing or on the label. Fan efficacy for fully ducted HRV, ERV, balanced and in-line fans shall be determined at a static pressure not less than 0.2 inch w.c. (49.8 Pa). Fan efficacy for ducted range hoods, bathroom and utility room fans shall be determined at a static pressure not less than 0.1 inch w.c. (24.9 Pa).

Exceptions:

1. Where ventilation fans are a component of a *listed* heating or cooling appliance.
2. Dryer exhaust duct power ventilators, domestic range hoods and domestic range booster fans that operate intermittently.
3. Fans in radon mitigation systems.
4. Fans not covered within the scope of the test methods referenced in Table C403.8.5.
5. Ceiling fans regulated under 10 CFR 430, Appendix U.

|  |  |  |  |
| --- | --- | --- | --- |
| **TABLE C403.8.5—LOW-CAPACITY VENTILATION FAN EFFICACYa** | | | |
| **SYSTEM TYPE** | **AIRFLOW RATE (CFM)** | **MINIMUM EFFICACY (CFM/WATT)** | **TEST PROCEDURE** |
| Balanced ventilation system without heat or energy recovery | Any | 1.2a | ASHRAE Standard 51  (ANSI/AMCA Standard 210) |
| HRV, ERV | Any | 1.2 | CAN/CSA 439 |
| Range hood | Any | 2.8 | ASHRAE 51  (ANSI/AMCA Standard 210) |
| In-line supply or exhaust fan | Any | 3.8 |
| Other exhaust fan | ≤ 90 | 2.8 |
| ≥ 90 and < 200 | 3.5 |
| ≥ 200 | 4.0 |
| For SI: 1 cfm/ft = 0.47 L/s.  a. For balanced systems, HRVs and ERVs, determine the efficacy as the outdoor airflow divided by the total fan power. | | | |

**C403.8.6 Fan control.** Controls shall be provided for fans in accordance with Section C403.8.6.1 and as required for specific systems provided in Section C403.

**C403.8.6.1 Fan airflow control.** Each cooling system listed in Table C403.8.6.1 shall be designed to vary the indoor fan airflow as a function of load and shall comply with the following requirements:

1. Direct expansion (DX) and chilled water cooling units that control the capacity of the mechanical cooling directly based on space temperature shall have not fewer than two stages of fan control. Low or minimum speed shall not be greater than 66 percent of full speed. At low or minimum speed, the *fan system* shall draw not more than 40 percent of the fan power at full fan speed. Low or minimum speed shall be used during periods of low cooling load and ventila- tion-only operation.
2. Other units including DX cooling units and chilled water units that control the space temperature by modulating the airflow to the space shall have modulating fan control. Minimum speed shall be not greater than 50 percent of full speed. At minimum speed the *fan system* shall draw not more than 30 percent of the power at full fan speed. Low or minimum speed shall be used during periods of low cooling load and ventilation-only operation.
3. Units that include an air-side economizer in accordance with Section C403.5 shall have not fewer than two speeds of fan control during economizer operation.

Exceptions:

* 1. Modulating fan control is not required for chilled water and evaporative cooling units with fan motors of less than 1 hp (0.746 kW) where the units are not used to provide *ventilation air* and the indoor fan cycles with the load.
  2. Where the volume of outdoor air required to comply with the ventilation requirements of the *International Mechanical Code* at low speed exceeds the air that would be delivered at the speed defined in Section C403.8.6, the minimum speed shall be selected to provide the required *ventilation air*.

|  |  |  |
| --- | --- | --- |
| **TABLE C403.8.6.1—COOLING SYSTEMS** | | |
| **COOLING SYSTEM TYPE** | **FAN MOTOR SIZE** | **MECHANICAL COOLING CAPACITY** |
| DX cooling | Any | ≥ 65,000 Btu/h |
| Chilled water and evaporative cooling | ≥ 1/4 hp | Any |
| For SI: 1 British thermal unit per hour = 0.2931 W; 1 hp = 0.746 kW. | | |

**C403.8.6.2 Intermittent exhaust control for bathrooms and toilet rooms.** Where an exhaust system serving a bathroom or toilet room is designed for intermittent operation, the exhaust system shall be provided with *manual* on capability and one or more of the following controls:

1. A timer control that has a minimum setpoint not greater than 30 minutes.
2. An occupant sensor control that automatically turns off exhaust fans within 30 minutes after all occupants have left the space.
3. A humidity control capable of manual or automatic adjustment from a minimum setpoint not greater than 50 percent to a maximum setpoint not greater than 80 percent relative humidity.
4. A contaminant control that responds to a particle or gaseous concentration.

**Exception:** Bathroom and toilet room exhaust systems serving as an integral component of an outdoor air ventilation system in Group R-2, R-3 and R-4 occupancies shall not be required to provide controls other than manual on capability.

An off setpoint shall not be used to comply with a minimum setpoint requirement.

**C403.9 Large-diameter ceiling fans.** Where provided, *large-diameter ceiling fans* shall be tested and *labeled* in accordance with AMCA 230 and shall meet the efficiency requirements of Table C403.9 and Section C403.9.1.

|  |  |  |
| --- | --- | --- |
| **TABLE C403.9—CEILING FAN EFFICIENCY REQUIREMENTSa** | | |
| **EQUIPMENT TYPE** | **MINIMUM EFFICIENCYb, c** | **TEST PROCEDURE** |
| Large-diameter ceiling fan for applications outside the USc | CFEI ≥ 1.00 at high (maximum) speed  CFEI ≥ 1.31 at 40% of high speed or the near- est speed that is not less than 40% of high speed | 10 CFR 430, Appendix U or AMCA 230 and AMCA 208 (for FEI calculations) |
| Large-diameter ceiling fan | CFEI ≥ 1.00 at high (maximum) speed; and CFEI ≥ 1.31 at 40% of high speed or the near- est speed that is not less than 40% of high speed | 10 CFR 430, Appendix U |
| 1. The minimum efficiency requirements at both high speed and 40% of maximum speed shall be met or exceeded to comply with this code. 2. Ceiling fans are regulated as consumer products by 10 CFR 430. 3. Chapter 6 contains a complete specification of the referenced test procedure, including the referenced year version of the test procedure. | | |

**C403.9.1 Ceiling Fan Energy Index (CFEI).** The Ceiling Fan Energy Index shall be calculated as the ratio of the electric input power of a reference *large-diameter ceiling fan* to the electric input power of the actual *large-diameter ceiling fan* as calculated in accordance with AMCA 208 with the following modifications to the calculations for the reference fan: using an airflow constant (Q) of 26,500 cfm (12.5 m3/s), a pressure constant (P) of 0.0027 inch of water (0.6719 Pa), and fan efficiency constant () of 42 percent.

**C403.10 Buildings with high-capacity space-heating gas boiler systems.** Gas hot water boiler systems for space heating with system input capacities of not less than 1,000,000 Btu/h (293 kW) and not greater than 10,000,000 Btu/h (2931 kW) in new *buildings* shall comply with Sections C403.10.1 and C403.10.2.

Exceptions:

* 1. Where 25 percent of the annual space heating requirement is provided by *on-site renewable energy*, site-recovered energy or heat recovery chillers.
  2. Space heating boilers installed in individual *dwelling units*.
  3. Where 50 percent or more of the design heating load is served using perimeter convective heating, radiant ceiling panels or both.
  4. Individual gas boilers with input capacity less than 300,000 Btu/h (88 kW) shall not be included in the calculations of the total system input or total system efficiency.

**C403.10.1 Boiler efficiency.** Gas hot water boilers shall have a thermal efficiency (Et) of not less than 90 percent where rated in accordance with the test procedures in Table C403.3.2(6). Systems with multiple boilers are allowed to meet this requirement where the space heating input provided by equipment with Et above or below 90 percent provides an input capacity-weighted average Et of not less than 90 percent. For boilers rated only for combustion efficiency, the calculation for the input capacity- weighted average Et shall use the combustion efficiency value.

**C403.10.2 Hot water distribution system design.** The hot water distribution system shall be designed to meet the following:

1. Coils and other heat exchangers shall be selected so that at design conditions the hot water return temperature entering the boilers is 120°F (49°C) or less.
2. Under all operating conditions, the water temperature entering the boiler is not greater than 120°F (49°C) or the flow rate of supply hot water that recirculates directly into the return system, such as by three-way valves or minimum flow bypass controls, shall be not greater than 20 percent of the design flow of the boilers.

**C403.11 Heat rejection equipment.** Heat rejection equipment, including air-cooled condensers, dry coolers, open-circuit cooling towers, closed-circuit cooling towers and evaporative condensers, shall comply with this section.

**Exception:** Heat rejection devices where energy usage is included in the equipment efficiency ratings listed in Tables C403.3.2(6) and C403.3.2(7).

**C403.11.1 Fan speed control.** Each *fan system* powered by an individual motor or array of motors with connected power, includ- ing the motor service factor, totaling 5 hp (3.7 kW) or more shall have controls and devices configured to automatically modulate the fan speed to control the leaving fluid temperature or condensing temperature and pressure of the heat rejection device. Fan motor power input shall be not more than 30 percent of design wattage at 50 percent of the design airflow.

Exceptions:

* 1. Fans serving multiple refrigerant or fluid cooling circuits.
  2. Condenser fans serving flooded condensers.

**C403.11.2 Multiple-cell heat rejection equipment.** Multiple-cell heat rejection equipment with variable speed fan drives shall be controlled to operate the maximum number of fans allowed that comply with the manufacturer’s requirements for all system components and so that all fans operate at the same fan speed required for the instantaneous cooling duty, as opposed to staged

on and off operation. The minimum fan speed shall be the minimum allowable speed of the fan drive system in accordance with the manufacturer’s recommendations.

**C403.11.3 Limitation on centrifugal fan open-circuit cooling towers.** Centrifugal fan open-circuit cooling towers with a combined rated capacity of 1,100 gpm (4164 L/m) or greater at 95°F (35°C) condenser water return, 85°F (29°C) condenser water supply, and 75°F (24°C) outdoor air wet-bulb temperature shall meet the energy efficiency requirement for axial fan open-circuit cooling towers listed in Table C403.3.2(7) .

**Exception:** Centrifugal open-circuit cooling towers that are designed with inlet or discharge *ducts* or require external sound attenuation.

**C403.11.4 Tower flow turndown.** Open-circuit cooling towers used on water-cooled chiller systems that are configured with multiple- or variable-speed condenser water pumps shall be designed so that all open-circuit cooling tower cells can be run in parallel with the larger of the flow that is produced by the smallest pump at its minimum expected flow rate or at 50 percent of the design flow for the cell.

**C403.11.5 Heat recovery for service water heating.** Condenser heat recovery shall be installed for heating or reheating of service hot water provided that the facility operates 24 hours a day, the total installed heat capacity of water-cooled systems exceeds 6,000,000 Btu/hr (1758 kW) of heat rejection, and the design service water heating load exceeds 1,000,000 Btu/h (293 kW).

The required heat recovery system shall have the capacity to provide the smaller of the following:

1. Sixty percent of the peak heat rejection load at design conditions.
2. The preheating required to raise the peak service hot water draw to 85°F (29°C).

Exceptions:

* 1. Facilities that employ condenser heat recovery for space heating or reheat purposes with a heat recovery design exceeding 30 percent of the peak water-cooled condenser load at design conditions.
  2. Facilities that provide 60 percent of their service water heating from site solar or site recovered energy or from other sources.

**C403.11.6 Heat recovery for space conditioning in health care facilities.** Where heated water is used for space heating, a heat pump chiller meeting the requirements of Table C403.3.2(15) for heat recovery and that uses the cooling system return water as the heat source shall be installed where the following are true:

1. The *building* is a Group I-2, Condition 2 occupancy.
2. The total design chilled water capacity for the Group I-2,Condition 2 occupancy, either air cooled or water cooled, required at cooling design conditions exceeds 3,600,000 Btu/h (1100 kw) of cooling.
3. Simultaneous heating, including reheat, and cooling occurs above 60°F (16°C) outdoor air temperature.

The heat recovery system shall have a cooling capacity of not less than 7 percent of the total design chilled water capacity of the Group I-2, Condition 2 occupancy at peak design conditions.

Exceptions:

* 1. *Buildings* that provide 60 percent or more of their reheat energy from *on-site renewable energy* or other site-recovered energy. *On-site renewable energy* used to meet Section C405.15.1 or C406.3.1 shall not be used to meet this exception.
  2. *Buildings* in Climate Zones 5C, 6B, 7 and 8.

**C403.12 Refrigeration equipment performance.** Refrigeration equipment performance shall be determined in accordance with Sections C403.12.1 and C403.12.2 for commercial refrigerators, freezers, refrigerator-freezers, *walk-in coolers*, *walk-in freezers* and refrigeration equipment. The energy use shall be verified through certification under an *approved* certification program or, where a certification program does not exist, the energy use shall be supported by data furnished by the equipment manufacturer.

**Exception:** *Walk-in coolers* and *walk-in freezers* regulated under federal law in accordance with Subpart R of DOE 10 CFR 431.

**C403.12.1 Commercial refrigerators, refrigerator-freezers and refrigeration.** Refrigeration equipment, defined in DOE 10 CFR Part 431.62, shall have an energy use in kWh/day not greater than the values of Table C403.12.1 when tested and rated in accor- dance with AHRI 1200.

**COMMERCIAL ENERGY EFFICIENCY**

**2024 INTERNATIONAL ENERGY CONSERVATION CODE®**

**125**

|  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE C403.12.1—MINIMUM EFFICIENCY REQUIREMENTS: COMMERCIAL REFRIGERATORS AND FREEZERS AND REFRIGERATION** | | | | | | | |
| **EQUIPMENT CATEGORY** | **CONDENSING UNIT CONFIGURATION** | **EQUIPMENT FAMILY** | **RATING TEMP., °F** | **OPERATING TEMP., °F** | **EQUIPMENT CLASSIFICATIONa, c** | **MAXIMUM DAILY ENERGY CONSUMPTION,**  **kWh/dayd, e** | **TEST STANDARD** |
| Remote condensing commercial refrigerators and commercial freezers | Remote (RC) | Vertical open (VOP) | 38 (M) | ≥ 32 | VOP.RC.M | 0.64 × TDA + 4.07 | AHRI 1200 |
| 0 (L) | < 32 | VOP.RC.L | 2.20 × TDA + 6.85 |
| Semivertical open (SVO) | 38 (M) | ≥ 32 | SVO.RC.M | 0.66 × TDA + 3.18 |
| 0 (L) | < 32 | SVO.RC.L | 2.20 × TDA + 6.85 |
| Horizontal open (HZO) | 38 (M) | ≥ 32 | HZO.RC.M | 0.35 × TDA + 2.88 |
| 0 (L) | < 32 | HZO.RC.L | 0.55 × TDA + 6.88 |
| Vertical closed transparent (VCT) | 38 (M) | ≥ 32 | VCT.RC.M | 0.15 × TDA + 1.95 |
| 0 (L) | < 32 | VCT.RC.L | 0.49 × TDA + 2.61 |
| Horizontal closed transparent (HCT) | 38 (M) | ≥ 32 | HCT.RC.M | 0.16 × TDA + 0.13 |
| 0 (L) | < 32 | HCT.RC.L | 0.34 × TDA + 0.26 |
| Vertical closed solid (VCS) | 38 (M) | ≥ 32 | VCS.RC.M | 0.10 × V + 0.26 |
| 0 (L) | < 32 | VCS.RC.L | 0.21 × V + 0.54 |
| Horizontal closed solid (HCS) | 38 (M) | ≥ 32 | HCS.RC.M | 0.10 × V + 0.26 |
| 0 (L) | < 32 | HCS.RC.L | 0.21 × V + 0.54 |
| Service over counter (SOC) | 38 (M) | ≥ 32 | SOC.RC.M | 0.44 × TDA + 0.11 |
| 0 (L) | < 32 | SOC.RC.L | 0.93 × TDA + 0.22 |
| Self-contained commercial refrigera- tors and commercial freezers with and without doors | Self-contained (SC) | Vertical open (VOP) | 38 (M) | ≥ 32 | VOP.SC.M | 1.69 × TDA + 4.71 | AHRI 1200 |
| 0 (L) | < 32 | VOP.SC.L | 4.25 × TDA + 11.82 |
| Semivertical open (SVO) | 38 (M) | ≥ 32 | SVO.SC.M | 1.70 × TDA + 4.59 |
| 0 (L) | < 32 | SVO.SC.L | 4.26 × TDA + 11.51 |
| Horizontal open (HZO) | 38 (M) | ≥ 32 | HZO.SC.M | 0.72 × TDA + 5.55 |
| 0 (L) | < 32 | HZO.RC.L | 1.90 × TDA + 7.08 |
| Vertical closed transparent (VCT) | 38 (M) | ≥ 32 | VCT.SC.M | 0.10 × V + 0.86 |
| 0 (L) | < 32 | VCT.SC.L | 0.29 × V + 2.95 |
| Vertical closed solid (VCS) | 38 (M) | ≥ 32 | VCS.SC.M | 0.05 × V + 1.36 |
| 0 (L) | < 32 | VCS.SC.L | 0.22 × V + 1.38 |
| Horizontal closed transparent (HCT) | 38 (M) | ≥ 32 | HCT.SC.M | 0.06 × V + 0.37 |
| 0 (L) | < 32 | HCT.SC.L | 0.08 × V + 1.23 |
| Horizontal closed solid (HCS) | 38 (M) | ≥ 32 | HCS.SC.M | 0.05 × V + 0.91 |
| 0 (L) | < 32 | HCS.SC.L | 0.06 × V + 1.12 |
| Service over counter (SOC) | 38 (M) | ≥ 32 | SOC.SC.M | 0.52 × TDA + 1.00 |
| 0 (L) | < 32 | SOC.SC.L | 1.10 × TDA + 2.10 |
| Self-contained commercial refrigera- tors with transparent doors for pull- down temperature applications | Self-contained (SC) | Pull-down (PD) | 38 (M) | ≥ 32 | PD.SC.M | 0.11 × V + 0.81 | AHRI 1200 |

|  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE C403.12.1—MINIMUM EFFICIENCY REQUIREMENTS: COMMERCIAL REFRIGERATORS AND FREEZERS AND REFRIGERATION—continued** | | | | | | | |
| **EQUIPMENT CATEGORY** | **CONDENSING UNIT CONFIGURATION** | **EQUIPMENT FAMILY** | **RATING TEMP., °F** | **OPERATING TEMP., °F** | **EQUIPMENT CLASSIFICATIONa, c** | **MAXIMUM DAILY ENERGY CONSUMPTION,**  **kWh/dayd, e** | **TEST STANDARD** |
| Commercial ice cream freezers | Remote (RC) | Vertical open (VOP) | -15 (I) | ≤ -5b | VOP.RC.I | 2.79 × TDA + 8.70 | AHRI 1200 |
| Semivertical open (SVO) | SVO.RC.I | 2.79 × TDA + 8.70 |
| Horizontal open (HZO) | HZO.RC.I | 0.70 × TDA + 8.74 |
| Vertical closed transpar- ent (VCT) | VCT.RC.I | 0.58 × TDA + 3.05 |
| Horizontal closed trans- parent (HCT) | HCT.RC.I | 0.40 × TDA + 0.31 |
| Vertical closed solid (VCS) | VCS.RC.I | 0.25 × V + 0.63 |
| Horizontal closed solid (HCS) | HCS.RC.I | 0.25 × V + 0.63 |
| Service over counter (SOC) | SOC.RC.I | 1.09 × TDA + 0.26 |
| Self-contained (SC) | Vertical open (VOP) | VOP.SC.I | 5.40 × TDA + 15.02 | AHRI 1200 |
| Semivertical open (SVO) | SVO.SC.I | 5.41 × TDA + 14.63 |
| Horizontal open (HZO) | HZO.SC.I | 2.42 × TDA + 9.00 |
| Vertical closed transpar- ent (VCT) | VCT.SC.I | 0.62 × TDA + 3.29 |
| Horizontal closed trans- parent (HCT) | HCT.SC.I | 0.56 × TDA + 0.43 |
| Vertical closed solid (VCS) | VCS.SC.I | 0.34 × V + 0.88 |
| Horizontal closed solid (HCS) | HCS.SC.I | 0.34 × V + 0.88 |
| Service over counter (SOC) | SOC.SC.I | 1.53 × TDA + 0.36 |
| For SI: 1 square foot = 0.0929 m2, 1 cubic foot = 0.02832 m3, °C = (°F – 32)/1.8.   1. The meaning of the letters in this column is indicated in the columns to the left. 2. Ice cream freezer is defined in DOE 10 CFR 431.62 as a commercial freezer that is designed to operate at or below -5 °F and that the manufacturer designs, markets or intends for the storing, displaying or dispensing of ice cream. 3. Equipment class designations consist of a combination [in sequential order separated by periods (AAA).(BB).(C)] of the following:    * (AAA)—An equipment family code (VOP = vertical open, SVO = semivertical open, HZO = horizontal open, VCT = vertical closed transparent doors, VCS = vertical closed solid doors, HCT = horizontal closed transparent doors, HCS = horizontal closed solid doors, and SOC = service over counter);    * (BB)—An operating mode code (RC = remote condensing and SC = self-contained); and    * (C)—A rating temperature code [M = medium temperature (38°F), L = low temperature (0°F), or I = ice cream temperature (-15°F)].    * For example, “VOP.RC.M” refers to the “vertical open, remote condensing, medium temperature” equipment class. 4. V is the volume of the case (ft3) as measured in AHRI 1200, Appendix C. 5. TDA is the total display area of the case (ft2) as measured in AHRI 1200, Appendix D. | | | | | | | |

**COMMERCIAL ENERGY EFFICIENCY**

**126**

**2024 INTERNATIONAL ENERGY CONSERVATION CODE®**

**C403.12.2 Walk-in coolers and walk-in freezers.** *Walk-in cooler* and *walk-in freezer* refrigeration systems, except for walk-in process cooling refrigeration systems as defined in DOE 10 CFR 431.302, shall meet the requirements of Tables C403.12.2.1(1), C403.12.2.1(2) and C403.12.2.1(3).

**C403.12.2.1 Performance standards.** *Walk-in coolers* and *walk-in freezers* shall meet the requirements of Tables C403.12.2.1(1), C403.12.2.1(2) and C403.12.2.1(3).

|  |  |  |  |
| --- | --- | --- | --- |
| **TABLE C403.12.2.1(1)—WALK-IN COOLER AND FREEZER DISPLAY DOOR EFFICIENCY REQUIREMENTSa** | | | |
| **CLASS DESCRIPTOR** | **CLASS** | **MAXIMUM ENERGY**  **CONSUMPTION (kWh/day)a** | **TEST PROCEDURE** |
| Display door, medium temperature | DD, M | 0.04 × Add + 0.41 | 10 CFR 431 |
| Display door, low temperature | DD, L | 0.15 × Add + 0.29 | 10 CFR 431 |
| a. Add is the surface area of the display door. | | | |

|  |  |  |  |
| --- | --- | --- | --- |
| **TABLE C403.12.2.1(2)—WALK-IN COOLER AND FREEZER NONDISPLAY DOOR EFFICIENCY REQUIREMENTSa** | | | |
| **CLASS DESCRIPTOR** | **CLASS** | **MAXIMUM ENERGY**  **CONSUMPTION (kWh/day)a** | **TEST PROCEDURE** |
| Passage door, medium temperature | PD, M | 0.05 × And + 1.7 | 10 CFR 431 |
| Passage door, low temperature | PD, L | 0.14 × And + 4.8 | 10 CFR 431 |
| Freight door, medium temperature | FD, M | 0.04 × And + 1.9 | 10 CFR 431 |
| Freight door, low temperature | FD, L | 0.12 × And + 5.6 | 10 CFR 431 |
| a. And is the surface area of the nondisplay door. | | | |

|  |  |  |  |
| --- | --- | --- | --- |
| **TABLE C403.12.2.1(3)—WALK-IN COOLER AND FREEZER REFRIGERATION SYSTEM EFFICIENCY REQUIREMENTS** | | | |
| **CLASS DESCRIPTOR** | **CLASS** | **MINIMUM ANNUAL WALK-IN ENERGY FACTOR (AWEF)**  **(Btu/W-h)a** | **TEST PROCEDURE** |
| Dedicated condensing, medium temperature, indoor system | DC.M.I | 5.61 | AHRI 1250 |
| Dedicated condensing, medium temperature, outdoor system | DC.M.O | 7.60 |
| Dedicated condensing, low temperature, indoor system, net capacity (*qnet*) < 6,500 Btu/h | DC.L.I < 6,500 | 9.091 × 10-5 × *qnet* + 1.81 |
| Dedicated condensing, low temperature, indoor system, net capacity (*qnet*) ≥ 6,500 Btu/h | DC.L.I ≥ 6,500 | 2.40 |
| Dedicated condensing, low temperature, outdoor system, net capacity (*qnet*) < 6,500 Btu/h | DC.L.O < 6,500 | 6.522 × 10-5 × *qnet* + 2.73 |
| Dedicated condensing, low temperature, outdoor system, net capacity (*qnet*) ≥ 6,500 Btu/h | DC.L.O ≥ 6,500 | 3.15 |
| Unit cooler, medium | UC.M | 9.00 |
| Unit cooler, low temperature, net capacity (*qnet*) < 15,500 Btu/h | UC.L < 15,500 | 1.575 × 10-5 × *qnet* + 3.91 |
| Unit cooler, low temperature, net capacity (*qnet*) ≥ 15,500 Btu/h | UC.L ≥ 15,500 | 4.15 |
| For SI: 1 British thermal unit per hour = 0.2931 W.  a. qnet is net capacity (Btu/h) as determined in accordance with AHRI 1250. | | | |

**C403.12.3 Refrigeration systems.** Refrigerated display cases, *walk-in coolers* or *walk-in freezers* that are served by remote compressors and remote condensers not located in a condensing unit, shall comply with Sections C403.12.3.1 and C403.12.3.2.

**Exception:** Systems where the working fluid in the refrigeration cycle goes through both subcritical and super-critical states (transcritical) or that use ammonia refrigerant are exempt.

**C403.12.3.1 Condensers serving refrigeration systems.** Fan-powered condensers shall comply with the following:

1. The design *saturated condensing temperatures* for air-cooled condensers shall not exceed the design dry-bulb temperature plus 10°F (5.6°C) for low-*temperature refrigeration systems*, and the design dry-bulb temperature plus 15°F (8°C) for *medium temperature refrigeration systems* where the *saturated condensing temperature* for blend refrig- erants shall be determined using the average of liquid and vapor temperatures as converted from the condenser drain pressure.
2. Condenser fan motors that are less than 1 hp (0.75 kW) shall use electronically commutated motors, permanent split- capacitor-type motors or 3-phase motors.
3. Condenser fans for air-cooled condensers, evaporatively cooled condensers, air- or water-cooled fluid coolers or cooling towers shall reduce fan motor demand to not more than 30 percent of design wattage at 50 percent of design air volume, and incorporate one of the following continuous variable speed fan control approaches:
   1. Refrigeration system condenser control for air-cooled condensers shall use variable setpoint control logic to reset the condensing temperature setpoint in response to ambient dry-bulb temperature.
   2. Refrigeration system condenser control for evaporatively cooled condensers shall use variable setpoint control logic to reset the condensing temperature setpoint in response to ambient wet-bulb temperature.
4. Multiple fan condensers shall be controlled in unison.
5. The minimum condensing temperature setpoint shall be not greater than 70°F (21°C).

**C403.12.3.2 Compressor systems.** Refrigeration compressor systems shall comply with the following:

1. Compressors and multiple-compressor system suction groups shall include control systems that use floating suction pressure control logic to reset the target suction pressure temperature based on the temperature requirements of the attached refrigeration display cases or walk-ins.

**Exception:** Controls are not required for the following:

1. Single-compressor systems that do not have variable capacity capability.
2. Suction groups that have a design saturated suction temperature of 30°F (-1.1°C) or higher, suction groups that comprise the high stage of a two-stage or cascade system, or suction groups that primarily serve chillers for secondary cooling fluids.
3. Liquid subcooling shall be provided for all low-temperature compressor systems with a design cooling capacity equal to or greater than 100,000 Btu (29.3 kW) with a design-saturated suction temperature of -10°F (-23°C) or lower. The subcooled liquid temperature shall be controlled at a maximum temperature setpoint of 50°F (10°C) at the exit of the subcooler using either compressor economizer (interstage) ports or a separate compressor suction group operating at a saturated suction temperature of 18°F (-7.8°C) or higher.
   1. Insulation for liquid lines with a fluid operating temperature less than 60°F (15.6°C) shall comply with Table C403.13.3(1) or C403.13.3(2).
4. Compressors that incorporate internal or external crankcase heaters shall provide a means to cycle the heaters off during compressor operation.

**C403.13 Construction of HVAC system elements.** *Ducts*, plenums, piping and other elements that are part of an HVAC system shall be constructed and insulated in accordance with Sections C403.13.1 through C403.13.3.1.

**C403.13.1 Duct and plenum insulation and sealing.** Supply and return air *ducts* and plenums shall be insulated with not less than R-6 insulation where located in unconditioned spaces and where located outside the *building* with not less than R-8 insula- tion in Climate Zones 0 through 4 and not less than R-12 insulation in Climate Zones 5 through 8. *Ducts* located underground beneath *buildings* shall be insulated as required in this section or have an equivalent *thermal distribution efficiency*. Underground *ducts* utilizing the *thermal distribution efficiency* method shall be *listed* and *labeled* to indicate the *R-value* equivalency. Where located within a *building thermal envelope* assembly, the *duct* or plenum shall be separated from the *building* exterior or uncondi- tioned or exempt spaces by not less than R-8 insulation in Climate Zones 0 through 4 and not less than R-12 insulation in Climate Zones 5 through 8.

Exceptions:

1. Where located within equipment.
2. Where the design temperature difference between the interior and exterior of the *duct* or plenum is not greater than 15°F (8°C).

*Ducts*, air handlers and filter boxes shall be sealed. Joints and seams shall comply with Section 603.9 of the *International Mechanical Code*.

**C403.13.2 Duct construction.** Ductwork shall be constructed and erected in accordance with the *International Mechanical Code*.

**C403.13.2.1 Low-pressure duct systems.** Longitudinal and transverse joints, seams and connections of supply and return *ducts* operating at a static pressure less than or equal to 2 inches water gauge (w.g.) (498 Pa) shall be securely fastened and sealed with welds, gaskets, mastics (adhesives), mastic-plus-embedded-fabric systems or tapes installed in accordance with the manufacturer’s instructions. Pressure classifications specific to the *duct system* shall be clearly indicated on the *construc- tion documents* in accordance with the *International Mechanical Code*.

**Exception:** Locking-type longitudinal joints and seams, other than the snap-lock and button-lock types, need not be sealed as specified in this section.

**C403.13.2.2 Medium-pressure duct systems.** *Ducts* and plenums designed to operate at a static pressure greater than 2 inches water gauge (w.g.) (498 Pa) but less than 3 inches w.g. (747 Pa) shall be insulated and sealed in accordance with Section C403.13.1. Pressure classifications specific to the *duct system* shall be clearly indicated on the *construction documents* in accor- dance with the *International Mechanical Code*.

**C403.13.2.3 High-pressure duct systems.** *Ducts* and plenums designed to operate at static pressures equal to or greater than 3 inches water gauge (747 Pa) shall be insulated and sealed in accordance with Section C403.13.1. In addition, *ducts* and plenums shall be leak tested in accordance with the SMACNA HVAC Air Duct Leakage Test Manual and shown to have a rate of *air leakage* (CL) less than or equal to 4.0 as determined in accordance with Equation 4-7.

**Equation 4-7** *CL* = *F/P*0.65

where:

*F* = The measured leakage rate in cfm per 100 square feet (9.3 m2) of duct surface.

*P* = The static pressure of the test.

Documentation shall be furnished demonstrating that representative sections totaling not less than 25 percent of the *duct*

area have been tested and that all tested sections comply with the requirements of this section.

**C403.13.3 Piping insulation.** Piping serving as part of a heating or cooling system shall be thermally insulated in accordance with Table C403.13.3(1) or C403.13.3(2).

Exceptions:

* 1. Factory-installed piping within HVAC equipment tested and rated in accordance with a test procedure referenced by this code.
  2. Factory-installed piping within room fan coils and unit ventilators tested and rated according to AHRI 440 (except that the sampling and variation provisions of Section 6.5 shall not apply) and AHRI 840, respectively.
  3. Piping that conveys fluids that have a design operating temperature range between 60°F (15°C) and 105°F (41°C).
  4. Piping that conveys fluids that have not been heated or cooled through the use of fossil fuels or electric power.
  5. Strainers, control valves, and balancing valves associated with piping 1 inch (25 mm) or less in diameter.
  6. Direct buried piping that conveys fluids at or below 60°F (15°C).
  7. In radiant heating systems, sections of piping intended by design to radiate heat.

|  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE C403.13.3(1)—MINIMUM PIPE INSULATION THICKNESS (in inches or *R*-value)a, c** | | | | | | | | |
| **FLUID OPERATING TEMPERATURE RANGE AND USAGE (°F)** | **INSULATION CONDUCTIVITY** | | **INCHES OR**  ***R*-VALUE** | **NOMINAL PIPE OR TUBE SIZE (inches)** | | | | |
| **Conductivity Btu**  **× in/(h × ft2 × °F)b** | **Mean Rating Temperature (°F)** | **< 1** | **1 to < 11/2** | **11/2 to < 4** | **4 to < 8** | **> 8** |
| **Minimum insulation thickness (inches)** | | | | |
| > 350 | 0.32–0.34 | 250 | Inches | 4.5 | 5.0 | 5.0 | 5.0 | 5.0 |
| *R*-value | R-32 | R-36 | R-34 | R-26 | R-21 |
| 251–350 | 0.29–0.32 | 200 | Inches | 3.0 | 4.0 | 4.5 | 4.5 | 4.5 |
| *R*-value | R-20 | R-29 | R-32 | R-24 | R-20 |
| 201–250 | 0.27–0.30 | 150 | Inches | 2.5 | 2.5 | 2.5 | 3.0 | 3.0 |
| *R*-value | R-17 | R-17 | R-17 | R-15 | R-13 |
| 141–200 | 0.25–0.29 | 125 | Inches | 1.5 | 1.5 | 2.0 | 2.0 | 2.0 |
| *R*-value | R-9 | R-9 | R-11 | R-10 | R-9 |
| 105–140 | 0.21–0.28 | 100 | Inches | 1.0 | 1.0 | 1.5 | 1.5 | 1.5 |
| *R*-value | R-5 | R-9 | R-8 | R-8 | R-7 |
| 40–60 | 0.21–0.27 | 75 | Inches | 0.5 | 0.5 | 1.0 | 1.0 | 1.0 |
| *R*-value | R-2 | R-2 | R-5 | R-5 | R-4 |
| < 40 | 0.20–0.26 | 50 | Inches | 0.5 | 1.0 | 1.0 | 1.0 | 1.5 |
| *R*-value | R-6 | R-9 | R-9 | R-8 | R-7 |
| For SI: 1 inch = 25.4 mm, °C = (°F – 32)/1.8.   1. For piping smaller than 11/2 inches and located in partitions within conditioned spaces, reduction of these thicknesses by 1 inch shall be permitted (before thickness adjust- ment required in Note b but not to a thickness less than 1 inch). 2. For insulation outside the stated conductivity range, the minimum thickness (*T*) shall be determined as follows:   *T* = *r*[(1 + *t/r*)*Kk* - 1] where:  *T* = Minimum insulation thickness.  *r* = Actual outside radius of pipe.  *t* = Insulation thickness listed in the table for applicable fluid temperature and pipe size.  *K* = Conductivity of alternate material at mean rating temperature indicated for the applicable fluid temperature (Btu × in/h × ft2 × °F).  *k* = The upper value of the conductivity range listed in the table for the applicable fluid temperature.   1. For direct-buried heating and hot water system piping, reduction of these thicknesses by 11/2 inches shall be permitted (before thickness adjustment required in Note b but not to thicknesses less than 1 inch). | | | | | | | | |

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| **TABLE C403.13.3(2)—MINIMUM PIPE INSULATION *R*-VALUEa** | | | | | |
| **FLUID OPERATING TEMPERATURE RANGE AND USAGE (°F)** | **NOMINAL PIPE OR TUBE SIZE (inches)** | | | | |
| **< 1** | **1 to < 11/2** | **11/2 to < 4** | **4 to < 8** | **≥ 8** |
| **Minimum Insulation *R*-Value** | | | | |
| > 350 | R-32 | R-36 | R-34 | R-26 | R-21 |
| 251–350 | R-20 | R-29 | R-32 | R-24 | R-20 |
| 201–250 | R-17 | R-17 | R-17 | R-15 | R-13 |
| 141–200 | R-9 | R-9 | R-11 | R-10 | R-9 |
| 105–140 | R-5 | R-9 | R-8 | R-8 | R-7 |
| 40–60 | R-2 | R-2 | R-5 | R-5 | R-4 |
| ≤ 40 | R-6 | R-9 | R-9 | R-8 | R-7 |
| For SI: 1 inch = 25.4 mm, R-1 = RSI-0.176228, °C = (°F – 32)/1.8.  a. The *R*-value of cylindrical piping insulation shall be determined as follows:  *R* = {*ro*[*ln*(*ro*/*ri*)]}/*k* where:  *R* = The interior R-value of the cylindrical piping insulation in Btu × ft2 × °F/h.  *ro* = The outer radius of the piping insulation in inches.  *ri* = The inner radius of the piping insulation in inches.  *k* = the thermal conductivity of the insulation material in Btu × in/h × ft2 × °F. | | | | | |

**C403.13.3.1 Protection of piping insulation.** Piping insulation exposed to the weather shall be protected from damage, including that caused by sunlight, moisture, equipment maintenance and wind. The protection shall provide shielding from solar radiation that can cause degradation of the material. The protection shall be removable and reuseable for not less than 6 inches (152 mm) from the connection to the equipment piping for maintenance. Adhesive tape shall not be permitted as a means of insulation protection.

**C403.14 Mechanical systems located outside of the building thermal envelope.** Mechanical systems providing heat outside of the *building thermal envelope* of a *building* shall comply with Sections C403.14.1 through C403.14.4.

**C403.14.1 Heating outside a building.** Systems installed to provide heat outside a *building* shall be radiant systems. Such heat- ing systems shall be controlled by an occupancy sensing device or a timer switch, so that the system is automatically de- energized when occupants are not present.

**C403.14.2 Snow- and ice-melt system controls.** Snow- and ice-melting systems shall include *automatic* controls configured to shut off the system when the pavement temperature is above 50°F (10°C) and precipitation is not falling, and an *automatic* or *manual* control that is configured to shut off when the outdoor temperature is above 40°F (4°C).

**C403.14.3 Roof and gutter deicing controls.** Roof and gutter deicing systems, including but not limited to self-regulating cable, shall include *automatic* controls that are configured to shut off the system when the outdoor temperature is above 40°F (4°C) and that include one of the following:

1. A moisture sensor configured to shut off the system in the absence of moisture.
2. A daylight sensor or other means configured to shut off the system between sunset and sunrise.

**C403.14.4 Freeze protection system controls.** Freeze protection systems, such as heat tracing of outdoor piping and heat exchangers, including self-regulating heat tracing, shall include *automatic* controls configured to shut off the systems when outdoor air temperatures are above 40°F (4°C) or when the conditions of the protected fluid will prevent freezing.

**C403.15 Dehumidification in spaces for plant growth and maintenance.** Equipment that dehumidifies *indoor grow* and *green- house* spaces shall be one or more of the following:

1. *Dehumidifiers* tested in accordance with the test procedure *listed* in DOE 10 CFR 430 and DOE 10 CFR 430, Subpart B, Appendix X or X1.
2. An integrated HVAC system with on-site heat recovery designed to fulfill not less than 75 percent of the annual energy for dehumidification reheat.
3. A chilled water system with on-site heat recovery designed to fulfill not less than 75 percent of the annual energy for dehu- midification reheat.
4. A solid or liquid desiccant dehumidification system for system designs that require a dewpoint of not more than 50°F (10°C).

**C403.16 Service water pressure-booster systems.** Service water pressure-booster systems shall be designed such that the follow- ing apply:

1. One or more pressure sensors shall be used to vary pump speed and/or start and stop pumps. The sensors shall either be located near the critical fixtures that determine the pressure required or logic shall be employed that adjusts the setpoint to simulate the operation of remote sensors.
2. No devices shall be installed for the purpose of reducing the pressure of all of the water supplied by any booster system pump or booster system, except for safety devices.
3. No booster system pumps shall operate when there is no service water flow.

**C403.17 Clean water pumps.** *Clean water pumps* meeting all the following criteria shall achieve a PEI rating not greater than 1.0:

* 1. Shaft input power is greater than or equal to 1.0 hp (0.75 kW) and less than or equal to 200 hp (149.1 kW) at its best efficiency point (BEP).
  2. Designated as either an end-suction close-coupled, end-suction frame-mounted, in-line, radially split vertical or submers- ible turbine pump.
  3. A flow rate of 25 gallons per minute (1.58 L/s) or greater at its BEP at full impeller diameter.
  4. Maximum head of 459 feet (139.9 m) at its BEP at full impeller diameter and the number of stages required for testing.
  5. Design temperature range from 14°F (-10°C) to 248°F (120°C).
  6. Designed to operate with one of the following. Note that for either Item 6.1 or 6.2, the driver and impeller must rotate at the same speed.
     1. A 2- or 4-pole induction motor.
     2. A noninduction motor with a speed of rotation operating range that includes speeds of rotation between 2,880 and 4,320 rpm and/or 1,440 and 2,160 rpm.
  7. For submersible turbine pumps, a 6-inch (152 mm) or smaller bowl diameter.
  8. For end-suction close-coupled pumps and end-suction frame-mounted/own bearings pumps, specific speeds less than or equal to 5,000 rpm when calculated using US customary units.

**Exceptions:** The following pumps are exempt from these requirements:

1. Fire pumps.
2. Self-priming pumps.
3. Prime-assisted pumps.
4. Magnet-driven pumps.
5. Pumps designed to be used in a nuclear facility subject to 10 CFR 50.
6. Pumps meeting the design and construction requirements set forth in US Military Specification MIL-P-17639F (1996), “Pumps, Centrifugal, Miscellaneous Service Naval Shipboard Use” (as amended); MIL-P-17840C (1986), “Pump, Centrifu- gal, Close Coupled, Navy Standard for Use on Naval Ships” (as amended); MIL-P-17881D (1972), “Pump, Centrifugal, Boiler Feed, (Multi Stage)” (as amended); MIL-P-18472G (1989), “Pumps, Centrifugal, Condensate, Feed Booster, Waste Heat Boiler, and Distilling Plant” (as amended); MIL-P-18682D (1984), “Pump, Centrifugal, Main Condenser Circulating, Naval Shipboard” (as amended).

SECTION C404 —SERVICE WATER HEATING

**C404.1 General.** This section covers the minimum efficiency of, and controls for, service water-heating equip- ment and insulation of service hot water piping.

**C404.2 Service water-heating equipment performance efficiency.** Water-heating equipment and hot water storage tanks shall meet the requirements of Table C404.2. The efficiency shall be verified through data furnished by the manufacturer of the equipment or through certification under an *approved* certification program. Water-heating equipment intended to be used to provide space heating shall meet the applicable provisions of Table C404.2.

**COMMERCIAL ENERGY EFFICIENCY**

**132**

**2024 INTERNATIONAL ENERGY CONSERVATION CODE®**

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| **TABLE C404.2—MINIMUM PERFORMANCE OF WATER-HEATING EQUIPMENT** | | | | | |
| **EQUIPMENT TYPE** | **SIZE CATEGORY** | **SUBCATEGORY OR RATING CONDITION** | **DRAW PATTERN** | **PERFORMANCE REQUIREDa** | **TEST PROCEDUREb** |
| Electric table-top water heatersc | ≤ 12 kW | ≥ 20 gal ≤ 120 gald | Very small Low Medium High | UEF ≥ 0.6323 – (0.0058 × *Vr*) UEF ≥ 0.9188 – (0.0031 × *Vr*) UEF ≥ 0.9577 – (0.0023 × *Vr*) UEF ≥ 0.9884 – (0.0016 × *Vr*) | DOE 10 CFR Part 430 App. E |
| Electric storage water heaterse, f: resistance and heat pump | ≤ 12 kW | ≥ 20 gal ≤ 55 galf | Very small Low Medium High | UEF ≥ 0.8808 – (0.0008 × *Vr*) UEF ≥ 0.9254 – (0.0003 × *Vr*) UEF ≥ 0.9307 – (0.0002 × *Vr*) UEF ≥ 0.9349 – (0.0001 × *Vr*) | DOE 10 CFR Part 430 App. E |
| ≤ 12 kW | > 55 gal ≤120 galf | Very small Low Medium High | UEF ≥ 1.9236 – (0.0011 × *Vr*) UEF ≥ 2.0440 – (0.0011 × *Vr*) UEF ≥ 2.1171 – (0.0011 × *Vr*) UEF ≥ 2.2418 – (0.0011 × *Vr*) | DOE 10 CFR Part 430 App. E |
| Electric storage water heaterse, f, m | > 12 kW | — | — | (0.3 + 27/*Vm*), %/h | DOE 10 CFR 431.106 App. B |
| Grid-enabled water heatersg | — | > 75 gald | Very small Low Medium High | UEF ≥ 1.0136 – (0.0028 × *Vr*) UEF ≥ 0.9984 – (0.0014 × *Vr*) UEF ≥ 0.9853 – (0.0010 × *Vr*) UEF ≥ 0.9720 – (0.0007 × *Vr*) | DOE 10 CFR 430 App. E |
| Electric instantaneous water heatersh | ≤ 12 kW | < 2 gald | Very small Low Medium High | UEF ≥ 0.91  UEF ≥ 0.91  UEF ≥ 0.91  UEF ≥ 0.92 | DOE 10 CFR Part 430 |
| > 12 kW & ≤ 58.6 kWi | ≤ 2 gal & ≤180ºF | All | UEF ≥ 0.80 | DOE 10 CFR Part 430 |
| Gas storage water heaterse, m | ≤ 75,000 Btu/h | ≥20 gal & ≤ 55 gald | Very small Low Medium High | UEF ≥ 0.3456 – (0.0020 × *Vr*) UEF ≥ 0.5982 – (0.0019 × *Vr*) UEF ≥ 0.6483 – (0.0017 × *Vr*) UEF ≥ 0.6920 – (0.0013 × *Vr*) | DOE 10 CFR Part 430 App. E |
| ≤ 75,000 Btu/h | > 55 gal & ≤ 100 gald | Very small Low Medium High | UEF ≥ 0.6470 – (0.0006 × *Vr*) UEF ≥ 0.7689 – (0.0005 × *Vr*) UEF ≥ 0.7897 – (0.0004 × *Vr*) UEF ≥ 0.8072 – (0.0003 × *Vr*) | DOE 10 CFR Part 430 App. E |
| > 75,000 Btu/h and  ≤ 105,000 Btu/hj, k | ≤ 120 gal & ≤180ºF | Very small Low Medium High | UEF ≥ 0.2674 – (0.0009 × *Vr*) UEF ≥ 0.5362 – (0.0012 × *Vr*) UEF ≥ 0.6002 – (0.0011 × *Vr*) UEF ≥ 0.6597 – (0.0009 × *Vr*) | DOE 10 CFR Part 430 App. E |
| > 105,000 Btu/hk | — | — | 80% *Et*  *SL*  *Q*  800 + 110 *V* Btu  h | DOE 10 CFR 431.106 |

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| **TABLE C404.2—MINIMUM PERFORMANCE OF WATER-HEATING EQUIPMENT—continued** | | | | | |
| **EQUIPMENT TYPE** | **SIZE CATEGORY** | **SUBCATEGORY OR RATING CONDITION** | **DRAW PATTERN** | **PERFORMANCE REQUIREDa** | **TEST PROCEDUREb** |
| Gas instantaneous water heatersi | > 50,000 Btu/h and  < 200,000 Btu/hk | < 2 gald | Very small Low Medium High | UEF ≥ 0.80  UEF ≥ 0.81  UEF ≥ 0.81  UEF ≥ 0.81 | DOE 10 CFR Part 430 App. E |
| ≥ 200,000 Btu/hk | < 10 gal | — | 80% *Et* | DOE 10 CFR 431.106 |
| ≥ 200,000 Btu/hk | ≥10 gal | — | 80% *Et*  *SL*  *Q*  800 + 110 *V* Btu  h |
| Oil storage water heaterse, m | ≤ 105,000 Btu/h | ≤ 50 gald | Very small Low Medium High | UEF = 0.2509 – (0.0012 × *Vr*) UEF = 0.5330 – (0.0016 × *Vr*) UEF = 0.6078 – (0.0016 × *Vr*) UEF = 0.6815 – (0.0014 × *Vr*) | DOE 10 CFR Part 430 |
| > 105,000 Btu/h and  ≤ 140,000 Btu/hl | ≤ 120 gal & ≤180ºF | Very small Low Medium High | UEF ≥ 0.2932 – (0.0015 × *Vr*) UEF ≥ 0.5596 – (0.0018 × *Vr*) UEF ≥ 0.6194 – (0.0016 × *Vr*) UEF ≥ 0.6740 – (0.0013 × *Vr*) | DOE 10 CFR Part 430 App. E |
| > 140,000 Btu/h | All | — | 80% *Et*  *SL*  *Q*  800 + 110 *V* Btu  h | DOE 10 CFR 431.106 |
| Oil instantaneous water heatersh, m | ≤ 210,000 Btu/h | < 2 gal | — | 80% *Et*  EF ≥ 0.59 – (0.0005 × *V*) | DOE 10 CFR Part 430 App. E |
| > 210,000 Btu/h | < 10 gal | — | 80% *Et* | DOE 10 CFR 431.106 |
| > 210,000 Btu/h | ≥ 10 gal | — | 78% *Et*  *SL*  *Q*  800 + 110 *V* Btu  h | DOE 10 CFR 431.106 |
| Hot water supply boilers, gas and oilh | ≥ 300,000 Btu/h and  < 12,500,000 Btu/h | < 10 gal | — | 80% *Et* | DOE 10 CFR 431.106 |
| Hot water supply boilers, gasi, m | ≥ 300,000 Btu/h and  < 12,500,000 Btu/h | ≥ 10 gal | — | 80% *Et*  *SL*  *Q*  800 + 110 *V* Btu  h | DOE 10 CFR 431.106 |
| Hot water supply boilers, oilh, m | ≥ 300,000 Btu/h and  < 12,500,000 Btu/h | ≥ 10 gal | — | 78% *Et*  *SL*  *Q*  800 + 110 *V* Btu  h | DOE 10 CFR 431.106 |
| Pool heaters, gasd | All | — f | — | 82% *Et* | DOE 10 CFR Part 430 App. P |
| Heat pump pool heaters | All | 50°F db and 44.2°F wb outdoor air 80.0°F entering water | — | 4.0 COP | DOE 10 CFR Part 430 App. P |
| Unfired storage tanks | All | — | — | Minimum insulation requirement R-12.5 (h × ft2 × °F)/Btu | (none) |

**COMMERCIAL ENERGY EFFICIENCY**

**2024 INTERNATIONAL ENERGY CONSERVATION CODE®**

**133**

**TABLE C404.2—MINIMUM PERFORMANCE OF WATER-HEATING EQUIPMENT—continued**

**COMMERCIAL ENERGY EFFICIENCY**

**134**

**2024 INTERNATIONAL ENERGY CONSERVATION CODE®**

For SI: 1 foot = 304.8 mm, 1 square foot = 0.0929 m2, °C = (°F – 32)/1.8, 1 British thermal unit per hour = 0.2931 W, 1 gallon = 3.785 L, 1 British thermal unit per hour per gallon = 0.078 W/L.

1. Thermal efficiency (*Et*) is a minimum requirement, while standby loss is a maximum requirement. In the standby loss equation, *V* is the rated volume in gallons and *Q* is the nameplate input rate in Btu/h. *Vm* is the measured volume in the tank in gallons. Standby loss for electric water heaters is in terms of %/h and denoted by the term “S,” and standby loss for gas and oil water heaters is in terms of Btu/h and denoted by the term “SL.” Draw pattern (DP) refers to the water draw profile in the Uniform Energy Factor (UEF) test. UEF and Energy Factor (EF) are minimum requirements. In the UEF standard equations, *Vr* refers to the rated volume in gallons.
2. Chapter 6 contains a complete specification, including the year version, of the referenced test procedure.
3. A tabletop water heater is a storage water heater that is enclosed in a rectangular cabinet with a flat top surface not more than 3 feet in height and has a ratio of input capacity (Btu/h) to tank volume (gal) < 4,000.
4. Water heaters or gas pool heaters in this category are regulated as consumer products by the US DOE, as defined in 10 CFR 430.
5. Storage water heaters have a ratio of input capacity (Btu/h) to tank volume (gal) < 4,000.
6. Efficiency requirements for electric storage water heaters ≤ 12 kW apply to both electric-resistance and heat pump water heaters. There are no minimum efficiency requirements for electric heat pump water heaters greater than 12 kW or for gas heat pump water heaters.
7. A grid-enabled water heater is an electric-resistance water heater that meets all of the following:
   1. Has a rated storage tank volume of more than 75 gallons.
   2. Is manufactured on or after April 16, 2015.
   3. Is equipped at the point of manufacture with an activation lock.
   4. Bears a permanent label applied by the manufacturer that complies with all of the following:
      1. Is made of material not adversely affected by water.
      2. Is attached by means of nonwater soluble adhesive.
      3. Advises purchasers and end users of the intended and appropriate use of the product with the following notice printed in 16.5 point Arial Narrow Bold font: “IMPORTANT INFORMATION: This water heater is intended only for use as a part of an electric thermal storage or demand response program. It will not provide adequate hot water unless enrolled in such a program and activated by your utility company or another program operator. Confirm the availability of a program in your local area before purchasing or installing this product.”
8. Instantaneous water heaters and hot water supply boilers have an input capacity (Btu/h) divided by storage volume (gal) ≥ 4,000 (Btu/h)/gal.
9. Electric instantaneous water heaters with input capacity >12 kW and ≤ 58.6 kW that (1) have a storage volume > 2 gallons, (2) are designed to provide outlet hot water at temperatures greater than 180°F, or (3) use three-phase power have no efficiency standard.
10. Gas storage water heaters with input capacity > 75,000 Btu/h and ≤ 105,000 Btu/h must comply with the requirements for the > 105,000 Btu/h if the water heater (1) has a storage volume > 120 gallons, (2) is designed to provide outlet hot water at temperatures greater than 180°F, or (3) uses three-phase power.
11. Refer to Section C404.2.1 for additional requirements for gas storage and instantaneous water heaters and gas hot water supply boilers.
12. Oil storage water heaters with input capacity > 105,000 Btu/h and ≤ 140,000 Btu/h must comply with the requirements for the > 140,000 Btu/h if the water heater either (1) has a storage volume > 120 gallons, (2) is designed to provide outlet hot water at temperatures greater than 180ºF, or (3) uses three-phase power.
13. Water heaters and hot water supply boilers with more than 140 gallons of storage capacity need not meet the standby loss requirement where: (1) the tank surface area is thermally insulated to R-12.5 or more, (2) there is no standing pilot light, and (3) for gas- or oil-fired storage water heaters, the heater is equipped with a fire damper or fan-assisted combustion.

**C404.2.1 High-input service water-heating systems.** Gas-fired *water heaters* installed in new *buildings* where the total input capacity provided by high-capacity gas-fired *water heaters* is 1,000,000 Btu/h (293 kW) or greater shall comply with either or both of the following requirements:

* 1. Where a singular piece of a high-capacity gas-fired *water heater* is installed, the water heater shall have a thermal effi- ciency, *Et*, of not less than 92 percent.
  2. Where multiple pieces of high-capacity gas-fired *water heaters* are connected to the same service water-heating system, the combined input-capacity-weighted average thermal efficiency, *Et*, shall be not less than 90 percent, and a minimum of 30 percent of the input to the high-capacity gas-fired *water heaters* in the service water-heating system shall have an *Et* of not less than 92 percent.

Exceptions:

1. The input rating of *water heaters* installed in individual *dwelling units* shall not be required to be included in the total input rating of service water-heating equipment for a *building*.
2. The input rating of water heaters with an input rating of not greater than 105,000 Btu/h (30.8 kW) shall not be required to be included in the total input rating of service water-heating equipment for a *building*.
3. Where not less than 25 percent of the annual *service water-heating* requirement is provided by *on-site renewable energy* or site-recovered energy, the minimum *Et* requirements of this section shall not apply. On-site renewable energy used to meet Section C405.15.1 or C406.3.1 shall not be used to meet this exception.

**C404.3 Heat traps for hot water storage tanks.** Storage tank-type *water heaters* and hot water storage tanks that have vertical water pipes connecting to the inlet and outlet of the tank shall be provided with integral *heat traps* at those inlets and outlets or shall have pipe-configured *heat traps* in the piping connected to those inlets and outlets. Tank inlets and outlets associated with solar water-heating system circulation loops shall not be required to have *heat traps*.

**C404.4 Service water heating system piping insulation.** *Service water heating* system piping shall be surrounded by uncom- pressed insulation. The wall thickness of the insulation shall be not less than the thickness shown in Table C404.4.1. Where the insulation thermal conductivity is not within the range in the table, Equation 4-8 shall be used to calculate the minimum insulation thickness:

**Equation 4-8** *talt* = *r* × [(1 + *ttable*/*r*)*kalt*/*kupper* - 1 where:

*talt* = Minimum insulation thickness of the alternate material (in) (mm).

*r* = Actual outside radius of the pipe (in) (mm).

*ttable* = Insulation thickness listed in this table for applicable fluid temperature and pipe size.

*kalt* = Thermal conductivity of the alternate material at mean rating temperature indicated for the applicable fluid tempera- ture [Btu × in/h × ft2 × °F] [W(m × °C)].

*kupper* = The upper value of the thermal conductivity range listed in this table for the applicable fluid temperature [Btu × in/h

× ft2 × °F] [W(m × °C)].

For nonmetallic piping thicker than Schedule 80 and having thermal resistance greater than that of steel pipe, reduced insulation thicknesses are permitted if documentation is provided showing that the pipe with the proposed insulation has no more heat trans- fer per foot (meter) than a steel pipe of the same size with the insulation thickness shown in the table.

**Exception:** Tubular pipe insulation shall not be required on the following:

1. Factory-installed piping within *water heaters* and hot water storage tanks.
2. Valves, pumps, strainers and threaded unions in piping that is 1 inch (25 mm) or less in nominal diameter.
3. Piping that conveys hot water that has not been heated through the use of fossil fuels or electricity.
4. Piping from user-controlled shower and bath mixing valves to the water outlets.
5. Cold-water piping of a *demand recirculation water system*.
6. Piping in existing buildings where *alterations* are made to existing *service water heating* systems where there is insuffi- cient space or access to meet the requirements.
7. Piping at locations where a vertical support of the piping is installed.
8. Where piping passes through a framing member if it requires increasing the size of the framing member.

**C404.4.1 Installation requirements.** The following piping shall be insulated per the requirements of this section:

1. Recirculating system piping, including the supply and return piping.
2. The first 8 feet (2.4 m) of outlet piping from:
   1. Storage *water heaters.*
   2. Hot water storage tanks.
   3. Any *water heater* and hot water supply boiler containing not less than 10 gallons (37.9 L) of water heated by a direct heat source, an indirect heat source, or both a direct heat source and an indirect heat source.
3. The first 8 feet (2.4 m) of branch piping connecting to recirculated, heat traced or impedance-heated piping.
4. The makeup water inlet piping between *heat traps* and the storage *water heaters* and the storage tanks they are serving, in a nonrecirculating *service water heating* storage system.
5. Hot water piping between multiple *water heaters*, between multiple hot water storage tanks, and between *water heaters*

and hot water storage tanks.

1. Piping that is externally heated (such as heat trace or impedance heating).
2. For direct-buried *service water heating* system piping, reduction of these thicknesses by 11/2 inches (38.1 mm) shall be permitted (before thickness adjustment required in Section C404.4) but not to thicknesses less than 1 inch (25.4 mm).

|  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE C404.4.1—MINIMUM PIPING INSULATION THICKNESS FOR SERVICE WATER HEATING SYSTEMSa** | | | | | | | |
| **SERVICE HOT-WATER TEMPERATURE RANGE** | **INSULATION THERMAL CONDUCTIVITY** | | **NOMINAL PIPE OR TUBE SIZE (inches)** | | | | |
| **Conductivity (Btu × in/h × ft2 × °F)** | **Mean Rating Temperature (°F)** | **< 1** | **1 to < 11/2** | **11/2 to < 4** | **4 to < 8** | **≥ 8** |
| **Insulation Thickness (inches)** | | | | |
| 105°F to 140°F | 0.22 to 0.28 | 100 | 1.0 | 1.0 | 1.5 | 1.5 | 1.5 |
| > 140°F to 200°F | 0.25 to 0.29 | 125 | 1.0 | 1.0 | 2.0 | 2.0 | 2.0 |
| > 200°F | 0.27 to 0.30 | 150 | 1.5 | 1.5 | 2.5 | 3.0 | 3.0 |
| For SI: 1 inch = 25.4 mm, 1 Btu/h × ft × °F = 1.73 W/mK, °C = [(°F) – 32]/1.8.  a. These thicknesses are based on energy efficiency considerations only. Additional insulation may be necessary for safety. | | | | | | | |

**C404.5 Heated water supply piping.** Heated water supply piping shall be in accordance with Section C404.5.1 or C404.5.2. The flow rate through 1/4-inch (6.4 mm) piping shall be not greater than 0.5 gpm (1.9 L/m). The flow rate through 5/16-inch (7.9 mm) piping shall be not greater than 1 gpm (3.8 L/m). The flow rate through 3/8-inch (9.5 mm) piping shall be not greater than 1.5 gpm (5.7 L/m).

**C404.5.1 Maximum allowable pipe length method.** The maximum allowable piping length from the nearest source of heated water to the termination of the fixture supply pipe shall be in accordance with the following. Where the piping contains more than one size of pipe, the largest size of pipe within the piping shall be used for determining the maximum allowable length of the piping in Table C404.5.1.

1. For a public lavatory faucet, use the “Public lavatory faucets” column in Table C404.5.1.
2. For all other plumbing fixtures and plumbing appliances, use the “Other fixtures and appliances” column in Table C404.5.1.

|  |  |  |  |
| --- | --- | --- | --- |
| **TABLE C404.5.1—PIPING VOLUME AND MAXIMUM PIPING LENGTHS** | | | |
| **NOMINAL PIPE SIZE**  **(inches)** | **VOLUME**  **(liquid ounces per foot length)** | **MAXIMUM PIPING LENGTH (feet)** | |
| **Public Lavatory Faucets** | **Other Fixtures and Appliances** |
| 1/4 | 0.33 | 6 | 50 |
| 5/16 | 0.5 | 4 | 50 |
| 3/8 | 0.75 | 3 | 50 |
| 1/2 | 1.5 | 2 | 43 |
| 5/8 | 2 | 1 | 32 |
| 3/4 | 3 | 0.5 | 21 |
| 7/8 | 4 | 0.5 | 16 |
| 1 | 5 | 0.5 | 13 |
| 11/4 | 8 | 0.5 | 8 |
| 11/2 | 11 | 0.5 | 6 |
| 2 or larger | 18 | 0.5 | 4 |
| For SI: 1 inch = 25.4 mm, 1 foot = 304.8 mm, 1 liquid ounce = 0.030 L, 1 gallon = 128 ounces. | | | |

**C404.5.2 Maximum allowable pipe volume method.** The water volume in the piping shall be calculated in accordance with Section C404.5.2.1. *Water heaters*, circulating water systems and heat trace temperature maintenance systems shall be consid- ered to be sources of heated water.

The volume from the nearest source of heated water to the termination of the fixture supply pipe shall be as follows:

1. For a public lavatory faucet: not more than 2 ounces (0.06 L).
2. For other plumbing fixtures or plumbing appliances; not more than 0.5 gallon (1.89 L).

**C404.5.2.1 Water volume determination.** The volume shall be the sum of the internal volumes of pipe, fittings, valves, meters and manifolds between the nearest source of heated water and the termination of the fixture supply pipe. The volume in the piping shall be determined from the “Volume” column in Table C404.5.1 or from Table C404.5.2.1. The volume contained within fixture shutoff valves, within flexible water supply connectors to a fixture fitting and within a fixture fitting shall not be included in the water volume determination. Where heated water is supplied by a recirculating system or heat-traced piping, the volume shall include the portion of the fitting on the branch pipe that supplies water to the fixture.

|  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE C404.5.2.1—INTERNAL VOLUME OF VARIOUS WATER DISTRIBUTION TUBING** | | | | | | | | | |
| **OUNCES OF WATER PER FOOT OF TUBE** | | | | | | | | | |
| **Nominal Size (inches)** | **Copper Type M** | **Copper Type L** | **Copper Type K** | **CPVC CTS SDR 11** | **CPVC SCH 40** | **CPVC SCH 80** | **PE-RT SDR 9** | **Composite ASTM F1281** | **PEX CTS SDR 9** |
| 3/8 | 1.06 | 0.97 | 0.84 | N/A | 1.17 | **—** | 0.64 | 0.63 | 0.64 |
| 1/2 | 1.69 | 1.55 | 1.45 | 1.25 | 1.89 | 1.46 | 1.18 | 1.31 | 1.18 |
| 3/4 | 3.43 | 3.22 | 2.90 | 2.67 | 3.38 | 2.74 | 2.35 | 3.39 | 2.35 |
| 1 | 5.81 | 5.49 | 5.17 | 4.43 | 5.53 | 4.57 | 3.91 | 5.56 | 3.91 |
| 11/4 | 8.70 | 8.36 | 8.09 | 6.61 | 9.66 | 8.24 | 5.81 | 8.49 | 5.81 |
| 11/2 | 12.18 | 11.83 | 11.45 | 9.22 | 13.20 | 11.38 | 8.09 | 13.88 | 8.09 |
| 2 | 21.08 | 20.58 | 20.04 | 15.79 | 21.88 | 19.11 | 13.86 | 21.48 | 13.86 |
| For SI: 1 foot = 304.8 mm, 1 inch = 25.4 mm, 1 liquid ounce = 0.030 L, 1 oz/ft 2= 305.15 g/m2. N/A = Not Available. | | | | | | | | | |

**C404.6 Heated-water circulating and temperature maintenance systems.** Heated-water circulation systems shall be in accor- dance with Section C404.6.1. Heat trace temperature maintenance systems shall be in accordance with Section C404.6.2. Controls for hot water storage shall be in accordance with Section C404.6.3. *Automatic* controls, temperature sensors and pumps shall be in a location with *access*. *Manual* controls shall be in a location with *ready access*.

**C404.6.1 Circulation systems.** Heated-water circulation systems shall be provided with a circulation pump. Gravity and thermo- syphon circulation systems shall be prohibited. The system return pipe shall be a dedicated return pipe. Controls shall be config- ured to automatically turn off the pump when the water in the circulation loop is at the desired temperature and when there is not a demand for hot water. Where a circulation pump serves multiple risers or piping zones, controls shall include self-actuating thermostatic balancing valves or another means of flow control to automatically balance the flow rate through each riser or piping zone.

**C404.6.1.1 Demand recirculation controls.** Demand recirculation water systems shall have controls that start the pump upon receiving a signal from the action of a user of a fixture or appliance, sensing the presence of a user of a fixture, or sensing the flow of hot or tempered water to a fixture fitting or appliance.

**C404.6.2 Heat trace systems.** Electric heat trace systems shall comply with IEEE 515.1. Controls for such systems shall be able to automatically adjust the energy input to the heat tracing to maintain the desired water temperature in the piping in accordance with the times when heated water is used in the occupancy. Heat trace shall be arranged to be turned off automatically when there is not a demand for hot water.

**C404.6.3 Controls for hot water storage.** The controls on pumps that circulate water between a *water heater* and a heated-water storage tank shall limit operation of the pump from heating cycle startup to not greater than 5 minutes after the end of the cycle.

**C404.7 Drain water heat recovery units.** Drain water heat recovery units shall comply with CSA B55.2. Potable water-side pressure loss shall be less than 10 psi (69 kPa) at maximum design flow. For *Group R* occupancies, the efficiency of drain water heat recovery unit efficiency shall be in accordance with CSA B55.1.

**C404.8 Energy consumption of pools and permanent spas.** The energy consumption of pools and permanent spas shall be controlled by the requirements in Sections C404.8.1 through C404.8.3.

**C404.8.1 Heaters.** The electric power to all heaters shall be controlled by an on-off switch that is an integral part of the heater, mounted on the exterior of the heater, or external to and within 3 feet (914 mm) of the heater in a location with *ready access*. Operation of such switch shall not change the setting of the heater *thermostat*. Such switches shall be in addition to a circuit breaker for the power to the heater. Gas-fired heaters shall not be equipped with continuously burning ignition pilots.

**C404.8.2 Time switches.** Time switches or other control methods that can automatically turn off and on heaters and pump motors according to a preset schedule shall be installed for heaters and pump motors. Heaters and pump motors that have built- in time switches shall be in compliance with this section.

Exceptions:

* 1. Where public health standards require 24-hour pump operation.
  2. Pumps that operate solar- and waste-heat-recovery pool heating systems.

**C404.8.3 Covers.** Outdoor heated pools and outdoor permanent spas shall be provided with a vapor-retardant cover or other

*approved* vapor-retardant means.

**Exception:** Where more than 75 percent of the energy for heating, computed over an operating season of not fewer than 3 calendar months, is from a heat pump or an on-site renewable energy system, covers or other vapor-retardant means shall not be required. *On-site renewable energy* used to meet Section C405.15.1 or C406.3.1 shall not be used to meet this exception.

**C404.9 Portable spas.** The energy consumption of electric-powered portable spas shall be controlled by the requirements of APSP 14.

SECTION C405 —ELECTRICAL POWER AND LIGHTING SYSTEMS

**C405.1 General.** Electrical power and lighting systems and generation shall comply with this section. General lighting shall consist of all lighting included when calculating the total connected interior lighting power in accordance with Section C405.3.1 and which does not require specific application controls in accordance with Section C405.2.5.

**Exception:** *Dwelling units* and *sleeping units* that comply with Sections C405.2.10, C405.3.3 and C405.6.

**C405.2 Lighting controls.** Lighting systems in *interior parking areas* shall be provided with controls that comply with Section C405.2.9. All other lighting systems powered through the energy service for the *building* and build- ing site lighting for which the *building owner* is responsible shall be provided with controls that comply with Sections C405.2.1 through C405.2.8.

**Exceptions:** Lighting controls are not required for the following:

1. Spaces where an *automatic* shutoff could endanger occupant safety or security.
2. Interior exit stairways, interior exit ramps and exit passageways.
3. Emergency lighting that is automatically off during normal operations.
4. Emergency lighting required by the *International Building Code* in exit access components that are not provided with fire alarm systems.
5. Up to 0.02 watts per square foot (0.22 W/m2) of lighting in exit access components that are provided with fire alarm systems.

**C405.2.1 Occupant sensor controls.** Occupant *sensor controls* shall be installed to control lights in the following space types:

1. Classrooms/lecture/training rooms.
2. *Computer room*, *data center.*
3. Conference/meeting/multipurpose rooms.
4. Copy/print rooms.
5. Lounges/breakrooms.
6. Medical supply room in a health care facility.
7. Enclosed offices.
8. Laundry/washing area.
9. Open plan office areas.
10. Restrooms.
11. Storage rooms.
12. Telemedicine room in a health care facility.
13. Locker rooms.
14. Corridors.
15. Warehouse storage areas.
16. Other spaces 300 square feet (28 m2) or less that are enclosed by floor-to-ceiling height partitions.

**Exception:** Luminaires that are required to have specific application controls in accordance with Section C405.2.5.

**C405.2.1.1 Occupant sensor control function.** Occupant sensor controls in warehouse storage areas shall comply with Section C405.2.1.2. Occupant sensor controls in open plan office areas shall comply with Section C405.2.1.3. Occupant sensor controls in corridors shall comply with Section C405.2.1.4. Occupant sensor controls for all other spaces specified in Section C405.2.1 shall comply with the following:

* 1. They shall automatically turn off lights within 20 minutes after all occupants have left the space.
  2. They shall be manual on or controlled to automatically turn on the lighting to not more than 50 percent power.
  3. They shall incorporate a manual control to allow occupants to turn off lights.

**Exception:** Full automatic-on controls with no manual control shall be permitted in *interior parking areas*, stairways, restrooms, locker rooms, lobbies, library stacks and areas where *manual* operation would endanger occupant safety or security.

**C405.2.1.2 Occupant sensor control function in warehouse storage areas.** Lighting in warehouse storage areas shall be controlled as follows:

1. Lighting in each aisleway shall be controlled independently of lighting in all other aisleways and open areas.
2. Occupant sensors shall automatically reduce lighting power within each controlled area to an unoccupied setpoint of not more than 50 percent of full power within 20 minutes after all occupants have left the controlled area.
3. Lights that are not turned off by occupant sensors shall be turned off by *time-switch control* complying with Section C405.2.2.1.
4. A *manual* control shall be provided to allow occupants to turn off lights in the space.

**C405.2.1.3 Occupant sensor control function in open plan office areas.** Occupant sensor controls in open plan office spaces less than 300 square feet (28 m 2) in area shall comply with Section C405.2.1.1. Occupant sensor controls in all other open plan office spaces shall comply with all of the following:

1. The controls shall be configured so that *general lighting* can be controlled separately in control zones with floor areas not greater than 600 square feet (55 m2) within the open plan office space.
2. *General lighting* in each control zone shall be permitted to automatically turn on upon occupancy within the control zone. *General lighting* in other unoccupied zones within the open plan office space shall be permitted to turn on to not more than 20 percent of full power or remain unaffected.
3. The controls shall automatically turn off *general lighting* in all control zones within 20 minutes after all occupants have left the open plan office space.

**Exception:** Where general lighting is turned off by *time-switch control* complying with Section C405.2.2.1.

1. General lighting in each control zone shall turn off or uniformly reduce lighting power to an unoccupied setpoint of not more than 20 percent of full power within 20 minutes after all occupants have left the control zone.

**C405.2.1.4 Occupant sensor control function in corridors.** Occupant sensor controls in corridors shall uniformly reduce lighting power to an unoccupied setpoint not more than 50 percent of full power within 20 minutes after all occupants have left the space.

**Exception:** Corridors provided with less than two footcandles of illumination on the floor at the darkest point with all lights on.

**C405.2.2 Time-switch controls.** Each area of the *building* that is not provided with *occupant sensor controls* complying with Section C405.2.1.1 shall be provided with *time-switch controls* complying with Section C405.2.2.1.

Exceptions:

1. Luminaires that are required to have specific application controls in accordance with Section C405.2.4.
2. Spaces where patient care is directly provided.

**C405.2.2.1 Time-switch control function.** *Time-switch controls* shall comply with all of the following:

1. Programmed to automatically turn off lights when the space is scheduled to be unoccupied.
2. Have a minimum 7-day clock.
3. Be capable of being set for seven different day types per week.
4. Incorporate an automatic holiday “shutoff” feature, which turns off all controlled lighting loads for not fewer than 24 hours and then resumes normally scheduled operations.
5. Have program backup capabilities, which prevent the loss of program and time settings for not fewer than 10 hours, if power is interrupted.
6. Include an override switch that complies with the following:
   1. The override switch shall be a *manual* control.
   2. The override switch, when initiated, shall permit the controlled lighting to remain on for not more than 2 hours.
   3. Any individual override switch shall control the lighting for an area not larger than 5,000 square feet (465 m2).
7. For spaces where schedules are not available, *time switch controls* are programmed to a schedule that turns off lights not less than 12 hours per day.

**Exception:** Within mall concourses, auditoriums, sales areas, manufacturing facilities and sports arenas:

1. The time limit shall be permitted to be greater than 2 hours, provided that the switch is a captive key device.
2. The area controlled by the override switch shall not be limited to 5,000 square feet (465 m2) provided that such area is less than 20,000 square feet (1860 m2).

**C405.2.3 Dimming controls.** Dimming controls complying with Section C405.2.3.1 are required for general lighting in the follow- ing space types:

* + 1. Classroom/lecture hall/training room.
    2. Conference/multipurpose/meeting room.
    3. In a dining area for bar/lounge or leisure, family dining.
    4. Laboratory.
    5. Lobby.
    6. Lounge/break room.
    7. Offices.
    8. Gymnasium/fitness center.
    9. Library reading room.
    10. In a health care facility for imaging rooms, exam rooms, nursery and nurses’ station.
    11. Spaces not provided with occupant sensor controls complying with Section C405.2.1.1.

**Exception:** Luminaires controlled by special application controls complying with Section C405.2.5.

**C405.2.3.1 Dimming control function.** Spaces required to have dimming control shall be provided with *manual* controls that allow lights to be dimmed from full output to 10 percent of full power or lower with continuous dimming, as well as turning off lights. *Manual* control shall be provided within each room to dim lights.

**Exceptions:** *Manual* dimming control is not required in spaces where *high-end trim* lighting controls are provided that comply with the following:

* + - 1. The calibration adjustment equipment is located for ready *access* only by authorized personnel.
      2. Lighting controls with ready *access* for users cannot increase the lighting power above the maximum level estab- lished by the *high-end trim* controls.

**C405.2.4 Daylight responsive controls.** *Daylight responsive controls* complying with Section C405.2.4.1 shall be provided to control the *general lighting* within *daylight zones* in the following spaces:

1. Spaces with a total of more than 75 watts of *general lighting* within primary sidelit *daylight zones* complying with Section C405.2.4.2.
2. Spaces with a total of more than 150 watts of *general lighting* within sidelit *daylight zones* complying with Section C405.2.4.2.
3. Spaces with a total of more than 75 watts of *general lighting* within toplit *daylight zones* complying with Section C405.2.4.3.

**Exceptions:** *Daylight responsive controls* are not required for the following:

* 1. Spaces in health care facilities where patient care is directly provided.
  2. Sidelit *daylight zones* on the first floor above grade in Group A-2 and Group M occupancies.
  3. Enclosed office spaces less than 250 square feet (23.2 m2).

**C405.2.4.1 Daylight responsive control function.** Where required, *daylight responsive controls* shall be provided within each space for control of lights in that space and shall comply with all of the following:

1. Lights in *toplit daylight zones* in accordance with Section C405.2.4.3 shall be controlled independently of lights in sidelit *daylight zones* in accordance with Section C405.2.4.2.
2. Lights in the primary sidelit *daylight zone* shall be controlled independently of lights in the secondary sidelit *daylight zone*.
3. *Daylight responsive controls* within each space shall be configured so that they can be calibrated from within that space by authorized personnel.
4. Calibration mechanisms shall be in a location with *ready access*.
5. *Daylight responsive controls* shall dim lights continuously from full light output to 15 percent of full light output or lower.
6. *Daylight responsive controls* shall be configured to completely shut off all controlled lights.
7. When occupant sensor controls have reduced the lighting power to an unoccupied setpoint in accordance with Sections C405.2.1.2 through C405.2.1.4, *daylight responsive controls* shall continue to adjust electric light levels in response to available daylight, but shall be configured to not increase the lighting power above the specified unoccu- pied setpoint.
8. Lights in *sidelit daylight zones* in accordance with Section C405.2.4.2 facing different cardinal orientations [within 45 degrees (0.79 rad) of due north, east, south, west] shall be controlled independently of each other.

Exceptions:

* 1. Within each space, up to 150 watts of lighting within the primary sidelit *daylight zone* is permitted to be controlled together with lighting in a primary sidelit *daylight zone* facing a different cardinal orientation.
  2. Within each space, up to 150 watts of lighting within the secondary sidelit *daylight zone* is permitted to be controlled together with lighting in a secondary sidelit *daylight zone* facing a different cardinal orientation.

**C405.2.4.2 Sidelit daylight zone.** The sidelit *daylight zone* is the floor area adjacent to vertical *fenestration* that complies with all of the following:

1. Where the *fenestration* is located in a wall, the primary sidelit *daylight zone* shall extend laterally to the nearest full- height wall, or up to 1.0 times the height from the floor to the top of the *fenestration*, and longitudinally from the edge of the *fenestration* to the nearest full-height wall, or up to 0.5 times the height from the floor to the top of the *fenestra- tion*, whichever is less, as indicated in Figure C405.2.4.2(1).
2. Where the *fenestration* is located in a *rooftop monitor*, the primary sidelit *daylight zone* shall extend laterally to the nearest obstruction that is taller than 0.7 times the ceiling height, or up to 1.0 times the height from the floor to the


bottom of the *fenestration*, whichever is less, and longitudinally from the edge of the *fenestration* to the nearest obstruction that is taller than 0.7 times the ceiling height, or up to 0.25 times the height from the floor to the bottom of the *fenestration*, whichever is less, as indicated in Figures C405.2.4.2(2) and C405.2.4.2(3).


1. Where the *fenestration* is located in a wall, the secondary sidelit *daylight zone* is directly adjacent to the primary sidelit *daylight zone* and shall extend laterally to 2.0 times the height from the floor to the top of the *fenestration* or to the nearest full height wall, whichever is less, and longitudinally from the edge of the *fenestration* to the nearest full height wall, or up to 0.5 times the height from the floor to the top of the *fenestration*, whichever is less, as indicated in Figure C405.2.4.2(1).
2. The area of the *fenestration* is not less than 24 square feet (2.23 m2).
3. The distance from the *fenestration* to any *building* or geological formation that would block *access to* daylight is greater than one-half of the height from the bottom of the *fenestration* to the top of the *building* or geologic formation.
4. The *visible transmittance* of the *fenestration* is not less than 0.20.
5. The projection factor (determined in accordance with Equation 4-4) for any overhanging projection that is shading the *fenestration* is not greater than 1.0 for *fenestration* oriented 45 degrees or less from true north and not greater than 1.5 for all other orientations.

A diagram of a house

Description automatically generated**FIGURE C405.2.4.2(1)—PRIMARY AND SECONDARY SIDELIT DAYLIGHT ZONES**

**FIGURE C405.2.4.2(2)—DAYLIGHT ZONE UNDER A ROOFTOP MONITOR**





ROOFTOP MONITOR

H

DAYLIGHT ZONE

OBSTRUCTION TALLER THAN

0.7 CEILING HEIGHT

0.25 H

(CH)

(a)

ROOFTOP MONITOR ABOVE

OBSTRUCTION

> 0.7 CH

CH

H

(b)

H


0.25 H


(a) Section view

(b) Plan view of daylight zone under a rooftop monitor

DAYLIGHT ZONE

**FIGURE C405.2.4.2(3)—DAYLIGHT ZONE UNDER A SLOPED ROOFTOP MONITOR**

OBSTRUCTION TALLER THAN



ROOFTOP MONITOR

H

DAYLIGHT ZONE

0.7 CEILING HEIGHT

0.25 H

(CH)

OBSTRUCTION

> 0.7 CH

(a)

(b)

CH

ROOFTOP MONITOR ABOVE

H

H

0.25 H

1. Section view
2. Plan view of daylight zone under a rooftop monitor


DAYLIGHT ZONE

**C405.2.4.3 Toplit daylight zone.** The *toplit daylight zone* is the floor area underneath a roof *fenestration* assembly that complies with all of the following:

1. The toplit *daylight zone* shall extend laterally and longitudinally beyond the edge of the roof *fenestration* assembly to the nearest obstruction that is taller than 0.7 times the ceiling height, or up to 0.7 times the ceiling height, whichever is less, as indicated in Figure C405.2.4.3.
2. Direct sunlight is not blocked from hitting the roof *fenestration* assembly at the peak solar angle on the summer solstice by *buildings* or geological formations.
3. The product of the *visible transmittance* of the roof *fenestration* assembly and the area of the rough opening of the roof *fenestration* assembly divided by the area of the *toplit* zone is not less than 0.008.

**FIGURE C405.2.4.3—TOPLIT DAYLIGHT ZONE**

OBSTRU




0.7 CH

ROOF FENESTRATION ASSEMBLY

0.7 CH

DAYLIGHT ZONE



CTION TALLER THAN

0.7 CEILING HEIGHT

(CH)

b)

0.7 CH

ROOF FENESTRATION ASSEMBLY ABOVE

0.7 CH

DAYLIGHT ZONE

0.7 CH

(a)

OBSTRUCTION

> 0.7 (CH)

CH

(

1. Section view


0.7 CH

1. Plan view of daylight zone under a roof fenestration assembly

**C405.2.4.4 Atriums.** *Daylight zones* at atrium spaces shall be established at the top floor surrounding the atrium and at the floor of the atrium space, and not on intermediate floors, as indicated in Figure C405.2.4.4.

**FIGURE C405.2.4.4—DAYLIGHT ZONES AT A MULTISTORY ATRIUM**

00ROOF FENESTRATION ASSEMBLY



ROOFTOP MONITOR

H1

DAYLIGHT ZONE


< H2

DAYLIGHT ZONE

CH1

CH2

H1



0.7 CH1

0.7 CH1

DAYLIGHT ZONE

< 0.7 CH2

< 0.7 CH2

DAYLIGHT ZONE

* 1. Section view of roof fenestration assembly at atrium
  2. Section view of roof monitor at atrium

H2

**C405.2.5 Specific application controls.** Specific application controls shall be provided for the following:

1. The following lighting shall be controlled by an occupant sensor complying with Section C405.2.1.1 or a *time-switch control* complying with Section C405.2.2.1. In addition, a *manual* control shall be provided to control such lighting sepa- rately from the *general lighting* in the space:
   1. Luminaires for which additional lighting power is claimed in accordance with Section C405.3.2.2.1.
   2. Display and accent, including lighting in display cases.
   3. Supplemental task lighting, including permanently installed under-shelf or under-cabinet lighting.
   4. Lighting equipment that is for sale or demonstration in lighting education.
2. Lighting for nonvisual applications, such as plant growth and food warming, shall be controlled by a *time switch control*

complying with Section C405.2.2.1 that is independent of the controls for other lighting within the room or space.

1. Task lighting for medical and dental purposes that is in addition to *general lighting* shall be provided with a *manual control*.
2. Lighting integrated into range hoods and exhaust fans shall be controlled independently of fans.

**C405.2.6 Manual controls.** Where required by this code, *manual* controls for lights shall comply with the following:

1. They shall be in a location with *ready access* to occupants.
2. They shall be located where the controlled lights are visible, or shall identify the area served by the lights and indicate their status.

**C405.2.7 Exterior lighting controls.** Exterior lighting systems shall be provided with controls that comply with Sections C405.2.7.1 through C405.2.7.4.

Exceptions:

* 1. Lighting for covered vehicle entrances to *buildings* where required for eye adaptation.
  2. Lighting controlled from within *dwelling units*.

**C405.2.7.1 Daylight shutoff.** Lights shall be automatically turned off when daylight is present and satisfies the lighting needs.

**C405.2.7.2 Building facade and landscape lighting.** *Building* facade and landscape lighting shall automatically shut off from not later than 1 hour after *building* or business closing to not earlier than 1 hour before *building* or business opening.

**C405.2.7.3 Lighting setback.** Lighting that is not controlled in accordance with Section C405.2.7.2 shall comply with the following:

1. Be controlled so that the total wattage of such lighting is automatically reduced by not less than 50 percent by selec- tively switching off or dimming luminaires at one of the following times:
   1. From not later than midnight to not earlier than 6 a.m.
   2. From not later than 1 hour after *building* or business closing to not earlier than 1 hour before *building* or business opening.
   3. During any time where activity has not been detected for 15 minutes or more.
2. Luminaires serving exterior parking areas and having a rated input wattage of greater than 40 watts and a mounting height of 24 feet (7315 mm) or less above the ground shall be controlled so that the total wattage of such lighting is automatically reduced by not less than 50 percent during any time where activity has not been detected for 15 minutes or more. Not more than 1,500 watts of lighting power shall be controlled together.

**C405.2.7.4 Exterior time-switch control function.** *Time-switch controls* for exterior lighting shall comply with the following:

1. They shall have a clock capable of being programmed for not fewer than 7 days.
2. They shall be capable of being set for seven different day types per week.
3. They shall incorporate an automatic holiday setback feature.
4. They shall have program backup capabilities that prevent the loss of program and time settings for a period of not less than 10 hours in the event that power is interrupted.

C405.2.8 Reserved.

C405.2.8.1 Demand responsive lighting controls function. Demand responsive controls for lighting shall be capable of the following:

1. Automatically reducing the output of controlled lighting to 80 percent or less of full power or light output upon receipt of a *demand response signal*.
2. Where *high-end trim* has been set, automatically reducing the output of controlled lighting to 80 percent or less of the

*high-end trim* setpoint upon receipt of a *demand response signal*.

1. Dimming controlled lights gradually and continuously over a period of not longer than 15 minutes to achieve their demand response setpoint.
2. Returning controlled lighting to its normal operational settings at the end of the demand response period.

**Exception:** Storage rooms and warehouse storage areas shall be permitted to switch off 25 percent or more of general light- ing power rather than dimming.

**C405.2.9 Interior parking area lighting control.** Interior parking area lighting shall be controlled by an *occupant sensor* comply- ing with Section C405.2.1.1 or a *time-switch control* complying with Section C405.2.2.1. Additional lighting controls shall be provided as follows:

1. Lighting power of each luminaire shall be automatically reduced by not less than 30 percent when there is no activity detected within a lighting zone for 20 minutes. Lighting zones for this requirement shall be not larger than 3,600 square feet (334.5 m2).

**Exception:** Lighting zones provided with less than 1.5 footcandles of illumination on the floor at the darkest point with all lights on are not required to have *automatic* light-reduction controls.

1. Where lighting for eye adaptation is provided at vehicle entrances to *buildings*, such lighting shall be separately controlled by a device that automatically reduces lighting power by at least 50 percent from sunset to sunrise.
2. The power to luminaires within 20 feet (6096 mm) of perimeter wall openings shall automatically reduce in response to daylight by at least 50 percent.

Exceptions:

* 1. Where the opening-to-wall ratio is less than 40 percent as viewed from the interior and encompassing the verti- cal distance from the driving surface to the lowest structural element.
  2. Where the distance from the opening to any exterior daylight blocking obstruction is less than one-half the height from the bottom of the opening or *fenestration* to the top of the obstruction.
  3. Where openings are obstructed by permanent screens or architectural elements restricting daylight entering the interior space.

**C405.2.10 Sleeping unit and dwelling unit lighting and switched receptacle controls.** *Sleeping units* and *dwelling units* shall be provided with lighting controls and switched receptacles as specified in Sections C405.2.10.1 and C405.2.10.2.

C405.2.10.1 Sleeping units and dwelling units in hotels, motels and vacation timeshare properties. *Sleeping units* and

*dwelling units* in hotels, motels and vacation timeshare properties shall be provided with the following:

1. Not less than two 125V, 15- and 20-amp switched receptacles in each room, except for bathrooms, kitchens, foyers, hallways and closets.
2. Lighting controls that automatically turn off all lighting and switched receptacles within 20 minutes after all occu- pants have left the unit.

**Exception:** Automatic shutoff is not required where captive key override controls all lighting and switched receptacles in units with five or fewer permanently installed lights and switched receptacles.

**C405.2.10.2 Sleeping units in congregate living facilities.** *Sleeping units* in *congregate living facilities* shall be provided with the following controls:

1. Lighting in bathrooms shall be controlled by an *occupant sensor control* that automatically turns off lights within 20 minutes after all occupants have left the space.
2. Each unit shall have a *manual* control by the entrance that turns off all lighting and switched receptacles in the unit, except for lighting in bathrooms and kitchens. The *manual* control shall be marked to indicate its function.

**C405.3 Interior lighting power requirements.** A *building* complies with this section where its total connected interior lighting power calculated under Section C405.3.1 is not greater than the interior lighting power allowance calculated under Section C405.3.2. *Sleeping units* and *dwelling units* shall comply with Section C405.3.3.

**C405.3.1 Total connected interior lighting power.** The total connected interior lighting power shall be determined in accor- dance with Equation 4-9.

**Equation 4-9** TCLP = [LVL + BLL + LED + TRK + Other]

where:

TCLP = Total connected lighting power (watts).

LVL = For luminaires with lamps connected directly to building power, such as line voltage lamps, the rated wattage of the lamp.

BLL = For luminaires incorporating a ballast or transformer, the rated input wattage of the ballast or transformer when operating that lamp.

LED = For light-emitting diode luminaires with either integral or remote drivers, the rated wattage of the luminaire.

TRK = For lighting track, cable conductor, rail conductor, and plug-in busway systems that allow the addition and reloca- tion of luminaires without rewiring, the wattage shall be one of the following:

* 1. The specified wattage of the luminaires, but not less than 8 W per linear foot (25 W/lin m).
  2. The wattage limit of the permanent current-limiting devices protecting the system.
  3. The wattage limit of the transformer supplying the system.

Other = The wattage of all other luminaires and lighting sources not covered previously and associated with interior lighting verified by data supplied by the manufacturer or other approved sources.

The connected power associated with the following lighting equipment and applications is not included in calculating total connected lighting power.

1. Emergency lighting automatically off during normal building operation.
2. Lighting in spaces specifically designed for use by occupants with special lighting needs, including those with visual impairment and other medical and age-related issues.
3. Mirror lighting in makeup or dressing areas used for video broadcasting, video or film recording, or live theatrical and music performance.
4. Task lighting for medical and dental purposes that is in addition to *general lighting*.
5. Display lighting for exhibits in galleries, museums and monuments that is in addition to *general lighting*.
6. Lighting in any location that is specifically used for video broadcasting, video or film recording, or live theatrical and music performance.
7. Lighting for photographic processes.
8. Lighting integral to equipment or instrumentation and installed by the manufacturer.
9. Task lighting for plant growth or maintenance.
10. Advertising signage or directional signage.
11. Lighting for food warming.
12. Lighting equipment that is for sale.
13. Lighting demonstration equipment in lighting education facilities.
14. Lighting approved because of safety considerations.
15. Lighting in retail display windows, provided that the display area is enclosed by ceiling-height partitions.
16. Furniture-mounted supplemental task lighting that is controlled by automatic shutoff.
17. Exit signs.
18. Antimicrobial lighting used for the sole purpose of disinfecting a space.
19. Lighting in *sleeping units* and *dwelling units*.
20. For exit access and exit stairways, including landings, where the applicable code requires an illuminance of 10 footcan- dles or more on the walking surface, the power in excess of the allowed power calculated according to Section C405.3.2.2 is not included.

**C405.3.2 Interior lighting power allowance.** The total interior lighting power allowance (watts) for an entire *building* shall be determined according to Table C405.3.2(1) using the Building Area Method or Table C405.3.2(2) using the Space-by-Space Method. The interior lighting power allowance for projects that involve only portions of a *building* shall be determined according to Table C405.3.2(2) using the Space-by-Space Method. *Buildings* with unfinished spaces shall use the Space-by-Space Method.

|  |  |
| --- | --- |
| **TABLE C405.3.2(1)—INTERIOR LIGHTING POWER ALLOWANCES: BUILDING AREA METHOD** | |
| **BUILDING AREA TYPE** | **LPD (watts/ft2)** |
| Automotive facility | 0.73 |
| Convention center | 0.64 |
| Courthouse | 0.75 |
| Dining: bar lounge/leisure | 0.74 |
| Dining: cafeteria/fast food | 0.70 |
| Dining: family | 0.65 |
| Dormitory | 0.52 |
| Exercise center | 0.72 |
| Fire station | 0.56 |
| Gymnasium | 0.75 |
| Health care clinic | 0.77 |
| Hospital | 0.92 |
| Hotel/Motel | 0.53 |
| Library | 0.83 |
| Manufacturing facility | 0.82 |
| Motion picture theater | 0.43 |
| Multiple-family | 0.46 |
| Museum | 0.56 |
| Office | 0.62 |
| Parking garage | 0.17 |
| Penitentiary | 0.65 |
| Performing arts theater | 0.82 |
| Police station | 0.62 |
| Post office | 0.64 |
| Religious building | 0.66 |
| Retail | 0.78 |
| School/university | 0.70 |
| Sports arena | 0.73 |
| Town hall | 0.67 |
| Transportation | 0.56 |
| Warehouse | 0.45 |
| Workshop | 0.86 |
| For SI: 1 watt per square foot = 10.76 w/m2. | |

|  |  |
| --- | --- |
| **TABLE C405.3.2(2)—INTERIOR LIGHTING POWER ALLOWANCES: SPACE-BY-SPACE METHOD** | |
| **COMMON SPACE TYPESa** | **LPD (watts/ft2)** |
| Atrium | |
| Less than or equal to 40 feet in height | 0.41 |
| Greater than 40 feet in height | 0.51 |
| Audience seating area | |
| In an auditorium | 0.57 |
| In a gymnasium | 0.23 |
| In a motion picture theater | 0.27 |
| In a penitentiary | 0.56 |
| In a performing arts theater | 1.09 |
| In a religious building | 0.72 |
| In a sports arena | 0.27 |
| Otherwise | 0.33 |
| Banking activity area | 0.56 |
| Breakroom (See Lounge/breakroom) | |
| Classroom/lecture hall/training room | |
| In a penitentiary | 0.74 |
| Otherwise | 0.72 |
| Computer room, data center | 0.75 |
| Conference/meeting/multipurpose room | 0.88 |
| Copy/print room | 0.56 |
| Corridor | |
| In a facility for the visually impaired (and not used primarily by the staff)b | 0.71 |
| In a hospital | 0.61 |
| Otherwise | 0.44 |
| Courtroom | 1.08 |
| Dining area | |
| In bar/lounge or leisure dining | 0.76 |
| In cafeteria or fast food dining | 0.36 |
| In a facility for the visually impaired (and not used primarily by the staff)b | 1.22 |
| In family dining | 0.52 |
| In a penitentiary | 0.35 |
| Otherwise | 0.42 |
| Electrical/mechanical room | 0.71 |
| Emergency vehicle garage | 0.51 |
| Food preparation area | 1.19 |
| Laboratory | |
| In or as a classroom | 1.05 |
| Otherwise | 1.21 |
| Laundry/washing area | 0.51 |
| Loading dock, interior | 0.88 |
| Lobby | |
| For an elevator | 0.64 |
| In a facility for the visually impaired (and not used primarily by the staff)b | 1.44 |
| In a motion picture theater | 0.20 |
| In a performing arts theater | 1.21 |
| Otherwise | 0.80 |

|  |  |
| --- | --- |
| **TABLE C405.3.2(2)—INTERIOR LIGHTING POWER ALLOWANCES: SPACE-BY-SPACE METHOD—continued** | |
| **COMMON SPACE TYPESa** | **LPD (watts/ft2)** |
| Locker room | 0.43 |
| Lounge/breakroom | |
| In a health care facility | 0.77 |
| Mother’s wellness room | 0.68 |
| Otherwise | 0.55 |
| Office | |
| Enclosed | 0.73 |
| Open plan | 0.56 |
| Parking area daylight transition zone | 1.06 |
| Parking area, interior | 0.11 |
| Pharmacy area | 1.59 |
| Restroom | |
| In a facility for the visually impaired (and not used primarily by the staff)b | 0.96 |
| Otherwise | 0.74 |
| Sales area | 0.85 |
| Seating area, general | 0.21 |
| Security screening general areas | 0.64 |
| Security screening in transportation facilities | 0.93 |
| Security screening transportation waiting area | 0.56 |
| Stairwell | 0.47 |
| Storage room | 0.35 |
| Vehicular maintenance area | 0.59 |
| Workshop | 1.17 |
| **BUILDING TYPE SPECIFIC SPACE TYPESa** | **LPD (watts/ft2)** |
| Automotive (see Vehicular maintenance area) | |
| Convention Center—exhibit space | 0.50 |
| Dormitory—living quarters | 0.48 |
| Facility for the visually impairedb | |
| In a chapel (and not used primarily by the staff) | 0.58 |
| In a recreation room (and not used primarily by the staff) | 1.20 |
| Fire station—sleeping quarters | 0.48 |
| Gaming establishments |  |
| High limits game | 1.68 |
| Slots | 0.54 |
| Sportsbook | 0.82 |
| Table games | 1.09 |
| Gymnasium/fitness center | |
| In an exercise area | 0.82 |
| In a playing area | 0.82 |
| Health care facility | |
| In an exam/treatment room | 1.33 |
| In an imaging room | 0.94 |
| In a medical supply room | 0.56 |
| In a nursery | 0.87 |
| In a nurse’s station | 1.07 |
| In an operating room | 2.26 |
| In a patient room | 0.78 |

|  |  |
| --- | --- |
| **TABLE C405.3.2(2)—INTERIOR LIGHTING POWER ALLOWANCES: SPACE-BY-SPACE METHOD—continued** | |
| **COMMON SPACE TYPESa** | **LPD (watts/ft2)** |
| Health care facility—continued | |
| In a physical therapy room | 0.82 |
| In a recovery room | 1.18 |
| In a telemedicine room | 1.44 |
| Library | |
| In a reading area | 0.86 |
| In the stacks | 1.18 |
| Manufacturing facility | |
| In a detailed manufacturing area | 0.75 |
| In an equipment room | 0.73 |
| In an extra-high-bay area (greater than 50 feet floor-to-ceiling height) | 1.36 |
| In a high-bay area (25–50 feet floor-to-ceiling height) | 1.24 |
| In a low-bay area (less than 25 feet floor-to-ceiling height) | 0.86 |
| Museum | |
| In a general exhibition area | 0.31 |
| In a restoration room | 1.24 |
| Performing arts theater—dressing room | 0.39 |
| Post office—sorting area | 0.71 |
| Religious buildings | |
| In a fellowship hall | 0.50 |
| In a worship/pulpit/choir area | 0.75 |
| Retail facilities | |
| In a dressing/fitting room | 0.45 |
| Hair salon | 0.65 |
| Nail salon | 0.75 |
| In a mall concourse | 0.57 |
| Massage space | 0.81 |
| Sports arena—playing area | |
| For a Class I facilityc | 2.86 |
| For a Class II facilityd | 1.98 |
| For a Class III facilitye | 1.29 |
| For a Class IV facilityf | 0.86 |
| Sports arena—pools |  |
| For a Class I facility | 2.20 |
| For a Class II facility | 1.47 |
| For a Class III facility | 0.99 |
| For a Class IV facility | 0.59 |
| Transportation facility | |
| Airport hanger | 1.36 |
| At a terminal ticket counter | 0.40 |
| In a baggage/carousel area | 0.28 |
| In an airport concourse | 0.49 |
| Passenger loading area | 0.71 |
| Warehouse—storage area | |
| For medium to bulky, palletized items | 0.33 |
| For smaller, hand-carried items | 0.69 |

|  |
| --- |
| **TABLE C405.3.2(2)—INTERIOR LIGHTING POWER ALLOWANCES: SPACE-BY-SPACE METHOD—continued** |
| For SI: 1 foot = 304.8 mm, 1 watt per square foot = 10.76 w/m2.   1. In cases where both a common space type and a building area specific space type are listed, the building area specific space type shall apply. 2. A ‘Facility for the Visually Impaired’ is a facility that is licensed or will be licensed by local or state authorities for senior long-term care, adult day care, senior support or people with special visual needs. 3. Class I facilities consist of professional facilities; and semiprofessional, collegiate or club facilities with seating for 5,000 or more spectators. 4. Class II facilities consist of collegiate and semiprofessional facilities with seating for fewer than 5,000 spectators, club facilities with seating for between 2,000 and 5,000 spec- tators, and amateur league and high school facilities with seating for more than 2,000 spectators. 5. Class III facilities consist of club, amateur league and high school facilities with seating for 2,000 or fewer spectators. 6. Class IV facilities consist of elementary school and recreational facilities; and amateur league and high school facilities without provision for spectators. |

**C405.3.2.1 Building Area Method.** For the Building Area Method, the interior lighting power allowance is calculated as follows:

1. For each building area type inside the *building*, determine the applicable building area type and the allowed lighting power density for that type from Table C405.3.2(1). For building area types not listed, select the building area type that most closely represents the use of that area. For the purposes of this method, an “area” shall be defined as all contiguous spaces that accommodate or are associated with a single building area type.
2. Determine the floor area for each building area type listed in Table C405.3.2(1) and multiply this area by the applica- ble value from Table C405.3.2(1) to determine the lighting power (watts) for each building area type. *Sleeping units* and *dwelling units* are excluded from lighting power allowance calculations by application of Section C405.3.3. The area of *sleeping units* and *dwelling units* is not included in the calculation.
3. The total interior lighting power allowance (watts) for the entire *building* is the sum of the lighting power from each building area type.

**C405.3.2.2 Space-by-Space Method.** Where a *building* has unfinished spaces, the lighting power allowance for the unfinished spaces shall be the total connected lighting power for those spaces, or 0.1 watts per square foot (1.08 w/m2), whichever is less. For the Space-by-Space Method, the interior lighting power allowance is calculated as follows:

1. For each space enclosed by partitions that are not less than 80 percent of the ceiling height, determine the applicable space type from Table C405.3.2(2). For space types not listed, select the space type that most closely represents the proposed use of the space. Where a space has multiple functions, that space may be divided into separate spaces.
2. Determine the total floor area of all the spaces of each space type and multiply by the value for the space type in Table C405.3.2(2) to determine the allowed lighting power (watts) for each space type. *Sleeping units* and *dwelling units* are excluded from lighting power allowance calculations by application of Section C405.3.3. The area of *sleeping units* and *dwelling units* is not included in the calculation.
3. The total interior lighting power allowance (watts) shall be the sum of the lighting power allowances for all space types.

**C405.3.2.2.1 Additional interior lighting power.** Where using the Space-by-Space Method, an increase in the interior light- ing power allowance is permitted for specific lighting functions. Additional power shall be permitted only where the specified lighting is installed and controlled in accordance with Section C405.2.5. These additional power allowances shall be used only for the luminaires serving the specific lighting function and shall not be used for any other purpose. An increase in the interior lighting power allowance is permitted in the following cases:

* 1. For lighting equipment to be installed in sales areas specifically to highlight merchandise, the additional lighting power allowance shall be the connected lighting power of the luminaires specifically highlighting merchandise, calculated in accordance with Equation 4-9, or the additional power allowance calculated in accordance with Equation 4-10, whichever is less.

**Equation 4-10** Additional lighting power allowance = 750 W + (Retail Area 1 × 0.40 W/ft2) + (Retail Area 2 × 0.40W/ft2) + (Retail Area 3 × 0.70 W/ft2) + (Retail Area 4 × 1.00 W/ft2)

For SI units:

Additional lighting power allowance = 750 W + (Retail Area 1 × 4.3 W/m2) + (Retail Area 2 × 4.3 W/m2) + (Retail Area 3 × 7.5 W/m2) + (Retail Area 4 × 10.8 W/m2)

where:

Retail Area 1 = The floor area for all products not listed in Retail Area 2, 3 or 4.

Retail Area 2 = The floor area used for the sale of vehicles, sporting goods and small electronics. Retail Area 3 = The floor area used for the sale of furniture, clothing, cosmetics and artwork.

Retail Area 4 = The floor area used for the sale of jewelry, crystal and china.

**Exception:** Other merchandise categories are permitted to be included in Retail Areas 2 through 4, provided that justification documenting the need for additional lighting power based on visual inspec- tion, contrast or other critical display is approved by the code official.

* 1. For spaces in which lighting is specified to be installed in addition to the *general lighting* for the purpose of decora- tive appearance or for highlighting art or exhibits, the additional lighting power allowance for that space shall be the smallest of the following:
     1. 0.66 W/ft2 ( 7.1W/m2) in lobbies,
     2. 0.55 W/ft2 ( 5.9 W/m 2) in other spaces, or
     3. The connected lighting power of the luminaires specifically for decorative appearance or for highlighting art or exhibits, calculated according to Equation 4-9.

**C405.3.3 Lighting power for sleeping units and dwelling units.** *Sleeping units* in Group I-2 occupancies that are patient rooms shall comply with Sections C405.3.1 and C405.3.2. For all other *sleeping units* and *dwelling units*, permanently installed lighting, including lighting integrated into range hoods and exhaust fans, shall be provided by lamps capable of operating with an efficacy of not less than 65 lumens per watt or luminaires capable of operating with an efficacy of not less than 45 lumens per watt.

Exceptions:

1. Lighting integral to other appliances.
2. Antimicrobial lighting used for the sole purpose of disinfecting.
3. Luminaires with an input rating of less than 3 watts.

**C405.4 Horticultural lighting.** Permanently installed luminaires shall have a *photosynthetic photon efficacy* of not less than 1.7 micromoles per joule (mol/J) for *horticultural lighting* in greenhouses and not less than 1.9 mol/J for all other *horticultural light- ing*. Luminaires for *horticultural lighting* in greenhouses shall be controlled by a device that automatically turns off the luminaire when sufficient daylight is available. Luminaires for *horticultural lighting* shall be controlled by a device that automatically turns off the luminaire at specific programmed times.

**Exception:** Cannabis facilities subject to 410 ILCS705/10-45, the Cannabis Regulation and Tax Act.

**C405.5 Exterior lighting power requirements.** The total connected exterior lighting power calculated in accordance with Section C405.5.1 shall be not greater than the exterior lighting power allowance calculated in accordance with Section C405.5.2.

**C405.5.1 Total connected exterior lighting power.** The total exterior connected lighting power shall be the total maximum rated wattage of all exterior lighting that is powered through the energy service for the *building* and building site lighting for which the *building owner* is responsible.

**Exception:** Lighting used for the following applications shall not be included.

1. Lighting *approved* because of safety considerations.
2. Emergency lighting automatically off during normal business operation.
3. Exit signs.
4. Specialized signal, directional and marker lighting associated with transportation.
5. Advertising signage or directional signage.
6. Integral to equipment or instrumentation and installed by its manufacturer.
7. Lighting in any location that is specifically used for video broadcasting, video or film recording, or live theatrical and music performances.
8. Athletic playing areas.
9. Temporary lighting.
10. Industrial production, material handling, transportation sites and associated storage areas.
11. Theme elements in theme/amusement parks.
12. Used to highlight features of art, public monuments and the national flag.
13. Lighting for water features and swimming pools.
14. Lighting controlled from within *sleeping units* and *dwelling units*.
15. Lighting of the exterior means of egress as required by the *International Building Code*.

**C405.5.2 Exterior lighting power allowance.** The exterior lighting power allowance (watts) is calculated as follows:

1. Determine the Lighting Zone (LZ) for the *building* according to Table C405.5.2(1), unless otherwise specified by the *code official*.
2. For each exterior area that is to be illuminated by lighting that is powered through the energy service for the *building* and building site lighting for which the building *owner* is responsible, determine the applicable area type from Table C405.5.2(2). For area types not listed, select the area type that most closely represents the proposed use of the area.
3. Determine the total area or length of each area type and multiply by the value for the area type in Table C405.5.2(2) to determine the lighting power (watts) allowed for each area type.
4. The total exterior lighting power allowance (watts) is the sum of the base site allowance determined according to Table C405.5.2(2), plus the watts from each area type.

|  |  |
| --- | --- |
| **TABLE C405.5.2(1)—EXTERIOR LIGHTING ZONES** | |
| **LIGHTING ZONE** | **DESCRIPTION** |
| 1 | Developed areas of national parks, state parks, forest land and rural areas |
| 2 | Areas predominantly consisting of residential zoning, neighborhood business districts, light industrial with limited night- time use and residential mixed-use areas |
| 3 | All other areas not classified as lighting zone 1, 2 or 4 |
| 4 | High-activity commercial districts in major metropolitan areas as designated by the local land use planning authority |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **TABLE C405.5.2(2)—LIGHTING POWER ALLOWANCES FOR BUILDING EXTERIORS** | | | | |
|  | **LIGHTING ZONES** | | | |
| **Zone 1** | **Zone 2** | **Zone 3** | **Zone 4** |
| Base Site Allowance | 160 W | 280 W | 400 W | 560 W |
| **Uncovered Parking Areas** | | | | |
| Parking area, exterior | 0.015 W/ft2 | 0.026 W/ft2 | 0.037 W/ft2 | 0.052 W/ft2 |
| **Building Grounds** | | | | |
| Walkways and ramps less | 0.50 W/linear foot | 0.50 W/linear foot | 0.55 W/linear foot | 0.60 W/linear foot |
| Plaza areas | 0.028 W/ft2 | 0.049 W/ft2 | 0.070 W/ft2 | 0.098 W/ft2 |
| Dining areas | 0.156 W/ft2 | 0.273 W/ft2 | 0.390 W/ft2 | 0.546 W/ft2 |
| Stairways | Exempt | Exempt | Exempt | Exempt |
| Pedestrian tunnels | 0.063 W/ft2 | 0.110 W/ft2 | 0.157 W/ft2 | 0.220 W/ft2 |
| Landscaping | 0.014 W/ft2 | 0.025 W/ft2 | 0.036 W/ft2 | 0.050 W/ft2 |
| **Building Entrances and Exits** | | | | |
| Pedestrian and vehicular entrances and exits | 5.6 W/linear foot of opening | 9.8 W/linear foot of opening | 14 W/linear foot of opening | 19.6 W/linear foot of opening |
| Entry canopies | 0.072 W/ft2 | 0.126 W/ft2 | 0.180 W/ft2 | 0.252W/ft2 |
| Loading docks | 0.104 W/ft2 | 0.182 W/ft2 | 0.260 W/ft2 | 0.364 W/ft2 |
| **Sales Canopies** | | | | |
| Free-standing and attached | 0.20 W/ft2 | 0.35 W/ft2 | 0.50 W/ft2 | 0.70 W/ft2 |
| **Outdoor Sales** | | | | |
| Open areas (including vehicle sales lots) | 0.072 W/ft2 | 0.126 W/ft2 | 0.180 W/ft2 | 0.252 W/ft2 |
| Street frontage for vehicle sales lots in addition to “open area” allowance | No allowance | 7.2 W/linear foot | 10.3 W/linear foot | 14.4 W/linear foot |
| For SI: 1 foot = 304.8 mm, 1 watt per square foot = 10.76 W/m2. W = Watt. | | | | |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **TABLE C405.5.2(3)—INDIVIDUAL LIGHTING POWER ALLOWANCES FOR BUILDING EXTERIORS** | | | | |
| **LIGHTING ZONES** | | | | |
|  | **Zone 1** | **Zone 2** | **Zone 3** | **Zone 4** |
| Building facades | No allowance | 0.075 W/ft2 of gross above-grade wall area | 0.113 W/ft2 of gross above-grade wall area | 0.15 W/ft2 of gross above-grade wall area |
| Automated teller machines (ATM) and night depositories | 90 W per location plus 35W per additional ATM per location | | | |
| Uncovered entrances and gatehouse inspection stations at guarded facilities | 0.144 W/ft2 of area | 0.252 W/ft2 of area | 0.360 W/ft2 of area | 0.504 W/ft2 of area |
| Uncovered loading areas for law enforcement, fire, ambulance and other emergency service vehicles | 0.104 W/ft2 of area | 0.182 W/ft2 of area | 0.260 W/ft2 of area | 0.364 W/ft2 of area |
| Drive-up windows and doors | 53 W per drive-through | 92 W per drive-through | 132 W per drive-through | 185 W per drive-through |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **TABLE C405.5.2(3)—INDIVIDUAL LIGHTING POWER ALLOWANCES FOR BUILDING EXTERIORS—continued** | | | | |
| **LIGHTING ZONES** | | | | |
|  | **Zone 1** | **Zone 2** | **Zone 3** | **Zone 4** |
| Parking area near 24-hour retail entrances | 80 W per main entry | 140 W per main entry | 200 W per main entry | 280 W per main entry |
| For SI: 1 watt per square foot = 10.76 W/m2. W = Watts. | | | | |

**C405.5.2.1 Additional exterior lighting power.** Additional exterior lighting power allowances are available for the specific lighting applications listed in Table C405.5.2(3). These additional power allowances shall be used only for the luminaires serv- ing these specific applications and shall not be used to increase any other lighting power allowance.

**C405.5.3 Gas lighting.** Gas-fired lighting appliances shall not be equipped with continuously burning pilot ignition systems.

**C405.6 Dwelling electrical meter.** Each *dwelling unit* located in a Group R-2 *building* shall have a separate electrical meter.

**C405.7 Electrical transformers.** Low-voltage dry-type distribution electric transformers shall meet the minimum efficiency require- ments of Table C405.7 as tested and rated in accordance with the test procedure *listed* in DOE 10 CFR 431. The efficiency shall be verified through certification under an *approved* certification program or, where a certification program does not exist, the equip- ment efficiency ratings shall be supported by data furnished by the transformer manufacturer.

**Exceptions:** The following transformers are exempt in accordance with the DOE definition of Distribution Transformers found in 10 CFR 431.192:

1. Transformers with a tap range of 20 percent or more.
2. Drive (isolation) transformers.
3. Rectifier transformers.
4. Auto-transformers.
5. Uninterruptible power system transformers.
6. Special impedance transformers.
7. Regulating transformers.
8. Sealed transformers.
9. Machine tool (control) transformers.
10. Welding transformers.
11. Grounding transformers.
12. Testing transformers.
13. Nonventilated transformers.

|  |  |  |  |
| --- | --- | --- | --- |
| **TABLE C405.7—MINIMUM NOMINAL EFFICIENCY LEVELS FOR**  **DOE 10 CFR 431 LOW-VOLTAGE DRY-TYPE DISTRIBUTION TRANSFORMERS** | | | |
| **SINGLE-PHASE TRANSFORMERSa** | | **THREE-PHASE TRANSFORMERSa** | |
| **kVAb** | **Efficiency (%)c** | **kVAb** | **Efficiency (%)c** |
| 15 | 97.70 | 15 | 97.89 |
| 25 | 98.00 | 30 | 98.23 |
| 37.5 | 98.20 | 45 | 98.40 |
| 50 | 98.30 | 75 | 98.60 |
| 75 | 98.50 | 112.5 | 98.74 |
| 100 | 98.60 | 150 | 98.83 |
| 167 | 98.70 | 225 | 98.94 |
| 250 | 98.80 | 300 | 99.02 |
| 333 | 98.90 | 500 | 99.14 |
| — | — | 750 | 99.23 |
| — | — | 1000 | 99.28 |
| 1. A low-voltage dry-type distribution transformer with a kVA rating not listed in the table shall have its minimum efficiency level determined by linear interpolation of the kVA and efficiency values listed in the table immediately above and below its kVA rating. Extrapolation shall not be used below the minimum values or above the maximum values shown for single-phase transformers and three-phase transformers. 2. kiloVolt-Amp rating. 3. Nominal efficiencies shall be established in accordance with the DOE 10 CFR 431 test procedure for low-voltage dry-type transformers. | | | |

**C405.8 Electric motors.** Electric motors shall meet the minimum efficiency requirements of Tables C405.8(1) through C405.8(4) when tested and rated in accordance with the DOE 10 CFR 431. The efficiency shall be verified through certification under an *approved* certification program or, where a certification program does not exist, the equipment efficiency ratings shall be supported by data furnished by the motor manufacturer.

**Exception:** The standards in this section shall not apply to the following exempt electric motors:

1. Air-over electric motors.
2. Component sets of an electric motor.
3. Liquid-cooled electric motors.
4. Submersible electric motors.
5. Inverter-only electric motors.
6. Definite-purpose machines within the scope of ANSI/NEMA MG 1, Part 18.

|  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE C405.8(1)—MINIMUM NOMINAL FULL-LOAD EFFICIENCY FOR NEMA DESIGN A,**  **NEMA DESIGN B, AND IEC DESIGN N MOTORS (EXCLUDING FIRE PUMP) ELECTRIC MOTORS AT 60 HZa, b** | | | | | | | | |
| **MOTOR HORSEPOWER (STANDARD KILOWATT EQUIVALENT)** | **NOMINAL FULL-LOAD EFFICIENCY (%) AS OF JUNE 1, 2016** | | | | | | | |
| **2 Pole** | | **4 Pole** | | **6 Pole** | | **8 Pole** | |
| **Enclosed** | **Open** | **Enclosed** | **Open** | **Enclosed** | **Open** | **Enclosed** | **Open** |
| 1 (0.75) | 77.0 | 77.0 | 85.5 | 85.5 | 82.5 | 82.5 | 75.5 | 75.5 |
| 1.5 (1.1) | 84.0 | 84.0 | 86.5 | 86.5 | 87.5 | 86.5 | 78.5 | 77.0 |
| 2 (1.5) | 85.5 | 85.5 | 86.5 | 86.5 | 88.5 | 87.5 | 84.0 | 86.5 |
| 3 (2.2) | 86.5 | 85.5 | 89.5 | 89.5 | 89.5 | 88.5 | 85.5 | 87.5 |
| 5 (3.7) | 88.5 | 86.5 | 89.5 | 89.5 | 89.5 | 89.5 | 86.5 | 88.5 |
| 7.5 (5.5) | 89.5 | 88.5 | 91.7 | 91.0 | 91.0 | 90.2 | 86.5 | 89.5 |
| 10 (7.5) | 90.2 | 89.5 | 91.7 | 91.7 | 91.0 | 91.7 | 89.5 | 90.2 |
| 15 (11) | 91.0 | 90.2 | 92.4 | 93.0 | 91.7 | 91.7 | 89.5 | 90.2 |
| 20 (15) | 91.0 | 91.0 | 93.0 | 93.0 | 91.7 | 92.4 | 90.2 | 91.0 |
| 25 (18.5) | 91.7 | 91.7 | 93.6 | 93.6 | 93.0 | 93.0 | 90.2 | 91.0 |
| 30 (22) | 91.7 | 91.7 | 93.6 | 94.1 | 93.0 | 93.6 | 91.7 | 91.7 |
| 40 (30) | 92.4 | 92.4 | 94.1 | 94.1 | 94.1 | 94.1 | 91.7 | 91.7 |
| 50 (37) | 93.0 | 93.0 | 94.5 | 94.5 | 94.1 | 94.1 | 92.4 | 92.4 |
| 60 (45) | 93.6 | 93.6 | 95.0 | 95.0 | 94.5 | 94.5 | 92.4 | 93.0 |
| 75 (55) | 93.6 | 93.6 | 95.4 | 95.0 | 94.5 | 94.5 | 93.6 | 94.1 |
| 100 (75) | 94.1 | 93.6 | 95.4 | 95.4 | 95.0 | 95.0 | 93.6 | 94.1 |
| 125 (90) | 95.0 | 94.1 | 95.4 | 95.4 | 95.0 | 95.0 | 94.1 | 94.1 |
| 150 (110) | 95.0 | 94.1 | 95.8 | 95.8 | 95.8 | 95.4 | 94.1 | 94.1 |
| 200 (150) | 95.4 | 95.0 | 96.2 | 95.8 | 95.8 | 95.4 | 94.5 | 94.1 |
| 250 (186) | 95.8 | 95.0 | 96.2 | 95.8 | 95.8 | 95.8 | 95.0 | 95.0 |
| 300 (224) | 95.8 | 95.4 | 96.2 | 95.8 | 95.8 | 95.8 | — | — |
| 350 (261) | 95.8 | 95.4 | 96.2 | 95.8 | 95.8 | 95.8 | — | — |
| 400 (298) | 95.8 | 95.8 | 96.2 | 95.8 | — | — | — | — |
| 450 (336) | 95.8 | 96.2 | 96.2 | 96.2 | — | — | — | — |
| 500 (373) | 95.8 | 96.2 | 96.2 | 96.2 | — | — | — | — |
| 1. Nominal efficiencies shall be established in accordance with DOE 10 CFR 431. 2. For purposes of determining the required minimum nominal full-load efficiency of an electric motor that has a horsepower or kilowatt rating between two horsepower or two kilowatt ratings listed in this table, each such motor shall be deemed to have a listed horsepower or kilowatt rating, determined as follows:    1. A horsepower at or above the midpoint between the two consecutive horsepowers shall be rounded up to the higher of the two horsepowers.    2. A horsepower below the midpoint between the two consecutive horsepowers shall be rounded down to the lower of the two horsepowers.    3. A kilowatt rating shall be directly converted from kilowatts to horsepower using the formula: 1 kilowatt = (1/0.746) horsepower. The conversion should be calculated to three significant decimal places, and the resulting horsepower shall be rounded in accordance with No. 1 or No. 2 above, as applicable. | | | | | | | | |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **TABLE C405.8(2)—MINIMUM NOMINAL FULL-LOAD EFFICIENCY FOR NEMA DESIGN C AND IEC DESIGN H MOTORS AT 60 HZa, b** | | | | | | |
| **MOTOR HORSEPOWER (STANDARD KILOWATT EQUIVALENT)** | **NOMINAL FULL-LOAD EFFICIENCY (%) AS OF JUNE 1, 2016** | | | | | |
| **4 Pole** | | **6 Pole** | | **8 Pole** | |
| **Enclosed** | **Open** | **Enclosed** | **Open** | **Enclosed** | **Open** |
| 1 (0.75) | 85.5 | 85.5 | 82.5 | 82.5 | 75.5 | 75.5 |
| 1.5 (1.1) | 86.5 | 86.5 | 87.5 | 86.5 | 78.5 | 77.0 |
| 2 (1.5) | 86.5 | 86.5 | 88.5 | 87.5 | 84.0 | 86.5 |
| 3 (2.2) | 89.5 | 89.5 | 89.5 | 88.5 | 85.5 | 87.5 |
| 5 (3.7) | 89.5 | 89.5 | 89.5 | 89.5 | 86.5 | 88.5 |
| 7.5 (5.5) | 91.7 | 91.0 | 91.0 | 90.2 | 86.5 | 89.5 |
| 10 (7.5) | 91.7 | 91.7 | 91.0 | 91.7 | 89.5 | 90.2 |
| 15 (11) | 92.4 | 93.0 | 91.7 | 91.7 | 89.5 | 90.2 |
| 20 (15) | 93.0 | 93.0 | 91.7 | 92.4 | 90.2 | 91.0 |
| 25 (18.5) | 93.6 | 93.6 | 93.0 | 93.0 | 90.2 | 91.0 |
| 30 (22) | 93.6 | 94.1 | 93.0 | 93.6 | 91.7 | 91.7 |
| 40 (30) | 94.1 | 94.1 | 94.1 | 94.1 | 91.7 | 91.7 |
| 50 (37) | 94.5 | 94.5 | 94.1 | 94.1 | 92.4 | 92.4 |
| 60 (45) | 95.0 | 95.0 | 94.5 | 94.5 | 92.4 | 93.0 |
| 75 (55) | 95.4 | 95.0 | 94.5 | 94.5 | 93.6 | 94.1 |
| 100 (75) | 95.4 | 95.4 | 95.0 | 95.0 | 93.6 | 94.1 |
| 125 (90) | 95.4 | 95.4 | 95.0 | 95.0 | 94.1 | 94.1 |
| 150 (110) | 95.8 | 95.8 | 95.8 | 95.4 | 94.1 | 94.1 |
| 200 (150) | 96.2 | 95.8 | 95.8 | 95.4 | 94.5 | 94.1 |
| 1. Nominal efficiencies shall be established in accordance with DOE 10 CFR 431. 2. For purposes of determining the required minimum nominal full-load efficiency of an electric motor that has a horsepower or kilowatt rating between two horsepower or two kilowatt ratings listed in this table, each such motor shall be deemed to have a listed horsepower or kilowatt rating, determined as follows:    1. A horsepower at or above the midpoint between the two consecutive horsepowers shall be rounded up to the higher of the two horsepowers.    2. A horsepower below the midpoint between the two consecutive horsepowers shall be rounded down to the lower of the two horsepowers.    3. A kilowatt rating shall be directly converted from kilowatts to horsepower using the formula: 1 kilowatt = (1/0.746) horsepower. The conversion should be calculated to three significant decimal places, and the resulting horsepower shall be rounded in accordance with No. 1 or No. 2 above, as applicable. | | | | | | |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **TABLE C405.8(3)—MINIMUM AVERAGE FULL-LOAD EFFICIENCY POLYPHASE SMALL ELECTRIC MOTORSa** | | | | |
| **MOTOR HORSEPOWER** | **OPEN MOTORS** | | | |
| **Number of Poles** | **2** | **4** | **6** |
| **Synchronous Speed (RPM)** | **3600** | **1800** | **1200** |
| 0.25 | — | 65.6 | 69.5 | 67.5 |
| 0.33 | — | 69.5 | 73.4 | 71.4 |
| 0.50 | — | 73.4 | 78.2 | 75.3 |
| 0.75 | — | 76.8 | 81.1 | 81.7 |
| 1 | — | 77.0 | 83.5 | 82.5 |
| 1.5 | — | 84.0 | 86.5 | 83.8 |
| 2 | — | 85.5 | 86.5 | N/A |
| 3 | — | 85.5 | 86.9 | N/A |
| N/A = Not Applicable.  a. Average full-load efficiencies shall be established in accordance with DOE 10 CFR 431. | | | | |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **TABLE C405.8(4)—MINIMUM AVERAGE FULL-LOAD EFFICIENCY FOR**  **CAPACITOR-START CAPACITOR-RUN AND CAPACITOR-START INDUCTION-RUN SMALL ELECTRIC MOTORSa** | | | | |
| **MOTOR HORSEPOWER** | **OPEN MOTORS** | | | |
| **Number of Poles** | **2** | **4** | **6** |
| **Synchronous Speed (RPM)** | **3600** | **1800** | **1200** |
| 0.25 | — | 66.6 | 68.5 | 62.2 |
| 0.33 | — | 70.5 | 72.4 | 66.6 |
| 0.50 | — | 72.4 | 76.2 | 76.2 |
| 0.75 | — | 76.2 | 81.8 | 80.2 |
| 1 | — | 80.4 | 82.6 | 81.1 |
| 1.5 | — | 81.5 | 83.8 | N/A |
| 2 | — | 82.9 | 84.5 | N/A |
| 3 | — | 84.1 | N/A | N/A |
| N/A = Not Applicable.  a. Average full-load efficiencies shall be established in accordance with DOE 10 CFR 431. | | | | |

**C405.9 Data centers and computer rooms.** Electrical equipment in *data centers* and *computer rooms* shall comply with this section.

**C405.9.1 Data centers.** Transformers, uninterruptable power supplies, motors and electrical power processing equipment in

*data centers* shall comply with Section 8 of ASHRAE 90.4 in addition to this code.

**C405.9.2 Computer rooms.** Uninterruptable power supplies in *computer rooms* shall comply with the requirements in Tables 8.5 and 8.6 of ASHRAE 90.4 in addition to this code.

**Exception:** AC-output UPS that utilizes standardized NEMA 1-15P or NEMA 5-15P input plug, as specified in ANSI/NEMA WD-6.

**C405.10 Vertical and horizontal transportation systems and equipment.** Vertical and horizontal transportation systems and equipment shall comply with this section.

**C405.10.1 Elevator cabs.** For the luminaires in each elevator cab, not including signals and displays, the sum of the lumens divided by the sum of the watts shall be not less than 35 lumens per watt. Ventilation fans in elevators that do not have their own air-conditioning system shall not consume more than 0.33 watts/cfm at the maximum rated speed of the fan. Controls shall be provided that will de-energize ventilation fans and lighting systems when the elevator is stopped, unoccupied and with its doors closed for over 15 minutes.

**C405.10.2 Escalators and moving walks.** Escalators and moving walks shall comply with ASME A17.1/CSA B44 and shall have

*automatic* controls that reduce speed as permitted in accordance with ASME A17.1/CSA B44 and applicable local code.

**Exception:** A variable voltage drive system that reduces operating voltage in response to light loading conditions is an alter- native to the reduced speed function.

**C405.10.2.1 Energy recovery.** Escalators shall be designed to recover electrical energy when resisting overspeed in the down direction.

**C405.11 Voltage drop.** The total *voltage drop* across the combination of customer-owned service conductors, feeder conductors and branch circuit conductors shall not exceed 5 percent.

**C405.12 Automatic receptacle control.** The following shall have *automatic* receptacle control complying with Section C405.12.1:

1. At least 50 percent of all 125V, 15- and 20-amp receptacles installed in enclosed offices, conference rooms, rooms used primarily for copy or print functions, breakrooms, classrooms and individual workstations, including those installed in modular partitions and module office workstation systems.
2. At least 25 percent of branch circuit feeders installed for modular furniture not shown on the *construction documents*.

**C405.12.1 Automatic receptacle control function.** *Automatic* receptacle controls shall comply with the following:

* 1. Either split controlled receptacles shall be provided with the top receptacle controlled, or a controlled receptacle shall be located within 12 inches (304.8 mm) of each uncontrolled receptacle.
  2. One of the following methods shall be used to provide control:
     1. A scheduled basis using a time-of-day operated control device that turns receptacle power off at specific programmed times and can be programmed separately for each day of the week. The control device shall be configured to provide an independent schedule for each portion of the *building* of not more than 5,000 square feet (464.5 m2) and not more than one floor. The occupant shall be able to manually override an area for not more than 2 hours. Any individual override switch shall control the receptacles of not more than 5,000 feet (1524 m).
     2. An *occupant sensor control* that shall turn off receptacles within 20 minutes of all occupants leaving a space.
     3. An automated signal from another control or alarm system that shall turn off receptacles within 20 minutes after determining that the area is unoccupied.
  3. All controlled receptacles shall be permanently marked in accordance with NFPA 70 and be uniformly distributed throughout the space.
  4. Plug-in devices shall not comply.

**Exceptions:** *Automatic* receptacle controls are not required for the following:

1. Receptacles specifically designated for equipment requiring continuous operation (24 hours per day, 365 days per year).
2. Spaces where an *automatic* control would endanger the safety or security of the room or building occupants.
3. Within a single modular office workstation, noncontrolled receptacles are permitted to be located more than 12 inches (304.8 mm), but not more than 72 inches (1828 mm) from the controlled receptacles serving that workstation.

**C405.13 Energy monitoring.** New *buildings* with a gross *conditioned floor area* of not less than 10,000 square feet (929 m2) shall be equipped to measure, monitor, record and report energy consumption in accordance with Sections C405.13.1 through C405.13.6 for load categories indicated in Table C405.13.2 and Sections C405.13.7 through C405.13.11 for end-use categories indicated in Table C405.13.8.

Exceptions:

1. *Dwelling units* in R-2 occupancies.
2. Individual tenant spaces are not required to comply with this section provided that the space has its own utility services and meters and has less than 5,000 square feet (464.5 m2) of *conditioned floor area*.

**C405.13.1 Electrical energy metering.** For electrical energy supplied to the *building* and its associated site, including but not limited to site lighting, parking, recreational facilities and other areas that serve the *building* and its occupants, meters or other measurement devices shall be provided to collect energy consumption data for each end-use category required by Section C405.13.2.

**C405.13.2 End-use electric metering categories.** Meters or other *approved* measurement devices shall be provided to collect energy use data for each end-use category indicated in Table C405.13.2. Where multiple meters are used to measure any end-use category, the data acquisition system shall total all of the energy used by that category. Not more than 5 percent of the design load for each of the end-use categories indicated in Table C405.13.2 shall be permitted to be from a load that is not within that category.

Exceptions:

* 1. HVAC and water heating equipment serving only an individual *dwelling unit* shall not require end-use metering.
  2. End-use metering shall not be required for fire pumps, stairwell pressurization fans or any system that operates only during testing or emergency.
  3. End-use metering shall not be required for an individual tenant space having a floor area not greater than 2,500 square feet (232 m2) where a dedicated source meter complying with Section C405.13.3 is provided.

|  |  |
| --- | --- |
| **TABLE C405.13.2—ELECTRICAL ENERGY USE CATEGORIES** | |
| **LOAD CATEGORY** | **DESCRIPTION OF ENERGY USE** |
| Total HVAC system | Heating, cooling and ventilation, including but not limited to fans, pumps, boilers, chillers and water heating. Energy used by 120-volt equipment, or by 208/120-volt equip- ment that is located in a building where the main service is 480/277-volt power, is permitted to be excluded from total HVAC system energy use. |
| Interior lighting | Lighting systems located within the building. |
| Exterior lighting | Lighting systems located on the building site but not within the building. |
| Plug loads | Devices, appliances and equipment connected to convenience receptacle outlets. |
| Process load | Any single load that is not included in an HVAC, lighting or plug load category and that exceeds 5 percent of the peak connected load of the whole building, including but not limited to data centers, manufacturing equipment and commercial kitchens. |
| Building operations and other miscellaneous loads | The remaining loads not included elsewhere in this table, including but not limited to vertical transportation systems, automatic doors, motorized shading systems, ornamen- tal fountains, fireplaces, swimming pools, spas and snow-melt systems. |
| Electric hot water heating for uses other than space conditioning | Electricity used to generate hot water.  **Exception:** Electric water heating with design capacity that is less than 10 percent of the building service rating. |

**C405.13.3 Electrical meters.** Meters or other measurement devices required by this section shall be configured to automatically communicate energy consumption data to the data acquisition system required by Section C405.13.4. Source meters shall be

allowed to be any digital-type meter. Lighting, HVAC or other building systems that can self-monitor their energy consumption shall be permitted instead of meters. Current sensors shall be permitted, provided that they have a tested accuracy of ±2 percent. Required metering systems and equipment shall have the capability to provide at least hourly data that is fully integrated into the data acquisition system and graphical energy report in accordance with Sections C405.13.4 and C405.13.5. Nonintrusive load monitoring (NILM) packages that extract energy consumption data from detailed electric waveform analysis shall be permitted to substitute for individual meters if the equivalent data is available for collection in Section C405.13.4 and reporting in Section C405.13.5.

**C405.13.4 Electrical energy data acquisition system.** A data acquisition system shall have the capability to store the data from the required meters and other sensing devices for a minimum of 36 months. The data acquisition system shall have the capability to store real-time energy consumption data and provide hourly, daily, monthly and yearly logged data for each end-use category required by Section C405.13.2. The data acquisition system shall have the capability of providing *building* total peak electric demand and the time(s) of day and time(s) per month at which the peak occurs. Peak demand shall be integrated over the same time period as the underlying whole-building meter reading rate.

**C405.13.5 Graphical energy report.** A permanent and readily available reporting mechanism shall be provided in the *building* for access by *building* operation and management personnel. The reporting mechanism shall have the capability to graphically provide the energy consumption for each end-use category required by Section C405.13.2 not less than every hour, day, month and year for the previous 36 months.

**C405.13.6 Renewable energy.** On-site renewable energy sources shall be metered with no less frequency than nonrenewable energy systems in accordance with Section C405.13.3.

**C405.13.7 Nonelectrical energy submetering.** For all nonelectrical energy supplied to the *building* and its associated site that serves the *building* and its occupants, submeters or other measurement devices shall be provided to collect energy consumption data for each end-use category required by Section C405.13.8.

Exceptions:

1. HVAC and water heating equipment serving only an individual *dwelling unit* shall not require end-use submetering.
2. End-use submetering shall not be required for fire pumps, stairwell pressurization fans or any system that operates only during testing or emergency.
3. End-use submetering shall not be required for an individual tenant space having a floor area not greater than 2,500 square feet (232 m2) where a dedicated source meter complying with Section C405.13.9 is provided.
4. Equipment powered primarily by solid fuels serving loads other than *building* heating and service water heating loads.

**C405.13.8 End-use nonelectrical submetering categories.** Submeters or other *approved* measurement devices shall be provided to collect energy use data for each end-use category indicated in Table C405.13.8. Where multiple submeters are used to measure any end-use category, the data acquisition system shall total all of the energy used by that category. Not more than 5 percent of the design load for each of the end-use categories indicated in Table C405.13.8 shall be permitted to be from a load that is not within that category.

|  |  |
| --- | --- |
| **TABLE C405.13.8—NONELECTRICAL ENERGY USE CATEGORIES** | |
| **END USE CATEGORY** | **DESCRIPTION OF END USE** |
| Total HVAC system | Heating and cooling systems, including but not limited to boilers, chillers and furnaces. District heating and cool- ing energy entering the building’s distribution system shall be monitored at the point of entry to the building distribution system. |
| Process loads | Any single load that is not included in the HVAC or service water heating categories where the rated fuel gas or fuel oil input of the load and that is not less than 5 percent of the sum of the rated fuel gas or fuel oil input of all monitored equipment, including but not limited to manufacturing equipment, process equipment, commercial kitchens, and commercial laundry equipment. |
| Other miscellaneous loads | The remaining loads not included elsewhere in this table, including but not limited to fireplaces, swimming pools, spas, gas lighting, and snow-melt systems. |
| Service water heating | Fuel used to heat potable water.  **Exception:** Water heating with design capacity that is less than 10 percent of the sum of the rated fuel gas or fuel oil input of all monitored equipment. |

**C405.13.9 Nonelectrical submeters.** Submeters or other measurement devices required by this section shall be configured to automatically communicate energy consumption data to the data acquisition system required by Section C405.13.10. Source submeters shall be allowed to be any digital-type meter that can provide a digital output to the data acquisition system. Required submetering systems and equipment shall be fully integrated into the data acquisition system and graphical energy report that updates at least hourly in accordance with Sections C405.13.10 and C405.13.11.

**C405.13.10 Nonelectrical energy data acquisition system.** A data acquisition system shall have the capability to store the data from the required submeters and other sensing devices for not less than 36 months. The data acquisition system shall have the

capability to store real-time energy consumption data and provide hourly, daily, monthly and yearly logged data for each end-use category required by Section C405.13.8. The data acquisition system shall have the capability of providing building total nonelec- trical peak demand and the time(s) of day and time(s) per month at which the peak occurs. Where applicable as determined by the authority having jurisdiction (AHJ), peak demand shall be integrated over the same time period as the underlying whole- building meter reading rate.

**C405.13.11 Graphical energy report.** A permanent and readily accessible reporting mechanism shall be provided in the *building* that is accessible by building operation and management personnel. The reporting mechanism shall have the capability to graph- ically provide the nonelectrical energy consumption for each end-use category required by Section C405.13.8 not less than every hour, day, month and year for the previous 36 months. The graphical report shall incorporate natural gas interval data from the submeter or the ability to enter gas utility bills into the report.

C405.14 Reserved.

**C405.15 Renewable energy systems.** *Buildings* in Climate Zones 0 through 7 shall comply with Sections C405.15.1 through C405.15.4.

**C405.15.1 On-site renewable energy systems.** *Buildings* shall be provided with on-site renewable electricity generation systems with a direct current (DC) nameplate power rating of not less than 0.75 watts per square foot (8.1 W/m2) multiplied by the sum of the gross *conditioned floor area* of all floors, not to exceed the combined gross *conditioned floor area* of the three largest floors.

**Exceptions:** The following *buildings* or building sites shall comply with Section C405.15.2:

* 1. A *building site* located where an unshaded flat plate collector oriented toward the equator and tilted at an angle from horizontal equal to the latitude receives an annual daily average incident solar radiation less than 1.1 kBtu/ft2 per day (3.5 kWh/m2/day).
  2. A *building* where more than 80 percent of the roof area is covered by any combination of permanent obstructions such as, but not limited to, mechanical equipment, vegetated space, access pathways or occupied roof terrace.
  3. Any *building* where more than 50 percent of the roof area is shaded from direct-beam sunlight by natural objects or by structures that are not part of the *building* for more than 2,500 annual hours between 8:00 a.m. and 4:00 p.m.
  4. A *building* with gross *conditioned floor area* less than 5,000 square feet (465 m2).

**C405.15.2 Off-site renewable energy.** *Buildings* that qualify for one or more of the exceptions to Section C405.15.1 or do not meet the requirements of Section C405.15.1 with an on-site renewable energy system shall procure off-site renewable electrical energy, in accordance with Sections C405.15.2.1 and C405.15.2.2, that shall be not less than the total off-site renewable electrical energy determined in accordance with Equation 4-11.

**Equation 4-11** *TREoff* = (*RENoff* × 0.75 W/ft2 × *FLRA* - *IREon*) × 15 where:

*TREoff* = Total off-site renewable electrical energy in kilowatt-hours (kWh) to be procured in accordance with Table C405.15.2.

*RENoff* = Annual off-site renewable electrical energy from Table C405.15.2, in units of kilowatt-hours per watt of array capacity.

FLRA = The sum of the gross conditioned floor area of all floors not to exceed the combined floor area of the three largest floors.

*IREon* = Annual on-site renewable electrical energy generation of a new on-site renewable energy system, to be installed as part of the building project, whose rated capacity is less than the rated capacity required in Section C405.15.1.

|  |  |
| --- | --- |
| **TABLE C405.15.2—ANNUAL OFF-SITE RENEWABLE ENERGY REQUIREMENTS** | |
| **CLIMATE ZONE** | **ANNUAL OFF-SITE RENEWABLE ELECTRICAL ENERGY (kWh/W)** |
| 1A, 2B, 3B, 3C, 4B and 5B | 1.75 |
| 0A, 0B, 1B, 2A, 3A and 6B | 1.55 |
| 4A, 4C, 5A, 5C, 6A and 7 | 1.35 |

**C405.15.2.1 Off-site procurement.** The building *owner,* as defined in the *International Building Code* , shall procure and be credited for the total amount of off-site renewable electrical energy, not less than required in accordance with Equation 4-11, with one or more of the following:

1. *Physical renewable energy power purchase agreement.*
2. *Financial renewable energy power purchase agreement.*
3. *Community renewable energy facility.*
4. Off-site renewable energy system owned by the building property owner.
5. *Renewable energy investment fund.*
6. *Green retail tariff.*

The generation source shall be located where the energy can be delivered to the *building site* by any of the following:

1. Direct connection to the off-site renewable energy facility.
2. The local utility or distribution entity.
3. An interconnected electrical network where energy delivery capacity between the generator and the building site is available.

**C405.15.2.2 Off-site contract.** The renewable energy shall be delivered or credited to the *building site* under an energy contract with a duration of not less than 10 years. The contract shall be structured to survive a partial or full transfer of owner- ship of the building property.

**C405.15.3 Renewable energy certificate (REC) documentation.** The property *owner* or owner’s authorized agent shall demon- strate that where renewable energy certificates (RECs) or energy attribute certificates (EACs) are associated with on-site and off- site renewable energy production required by Sections C405.15.1 and C405.15.2, all of the following criteria for RECs and EACs shall be met:

1. The RECs and EACs are retained and retired by or on behalf of the property owner or tenant for a period of not less than 15 years or the duration of the contract in Section C405.15.2.2, whichever is less.
2. The RECs and EACs are created within a 12-month period of the use of the REC.
3. The RECs and EACs are from a generating asset placed in service not more than 5 years before the issuance of the certifi- cate of occupancy.

**C405.15.4 Renewable energy certificate purchase.** A *building* that qualifies for one or more of the exceptions to Section C405.15.1, and where it can be demonstrated to the *code official* that the requirements of Section C405.15.2 cannot be met, the building owner shall contract the purchase of renewable electricity products before the certificate of occupancy is issued. The purchase of renewable electricity products shall comply with the Green-e Energy National Standard for renewable electricity products equivalent to five times the amount of total off-site renewable energy calculated in accordance with Equation 4-11.

**C405.16 Inverters.** Direct-current-to-alternating-current inverters serving on-site renewable energy systems or on-site electrical energy storage systems (ESS) shall be compliant with IEEE 1547 and UL 1741.

**C405.17 Electric infrastructure.** New Group R-2 occupancies that use fossil fuels for space heating, *service water heating*,

cooking or clothes drying shall install electric infrastructure in accordance with Section C105.2.2 and Sections C405.17.1 through C405.17.5.

**C405.17.1 Space heating.** Locations with piping for fossil fuel warm-air furnaces and fossil fuel boilers shall comply with Section C405.17.1.1 or C405.17.1.2, as applicable.

**Exception:** Where a branch circuit exists for space cooling equipment with the capacity to serve heat pump space heating equipment sized in accordance with the requirements of Section C403.1.1.

**C405.17.1.1 Low-capacity space heating.** Locations of fossil fuel warm-air furnaces with a capacity less than 225,000 Btu/hr (65.9 kW) and boilers with a capacity less than 300,000 Btu/hr (88 kW) shall be provided with an individual branch circuit in accordance

with all of the following:

1. The branch circuit conductors shall terminate within 6 feet (1829 mm) of the location of the space heating equipment and shall be in a location with *ready access*.
2. The branch circuit shall be sized to serve heat pump space heating equipment sized in accordance with the requirements of Section C403.1.1.
3. The branch circuit overcurrent device and the termination of the branch circuit shall be labeled, “For future heat pump space heating equipment.”

**C405.17.1.2 Other space heating equipment.** Locations of fossil fuel space heating equipment not covered under Section C405.17.1.1 shall be provided with a raceway in accordance with all of the following:

The raceway shall be continuous from a branch circuit panel to a junction box located within the same space as the equipment or, where the equipment is located on the exterior of the building, within 3 feet (914 mm) of the equipment.

The junction box, raceway and bus bar in the electric panel and conductors serving the electrical panel shall be sized to serve electric space heating equipment sized to serve the same load as the fossil fuel space heating equipment.

The electrical panel shall have sufficient reserved physical space for branch circuit overprotection devices sized to serve electric equipment sized to serve the same load as the fossil fuel space heating appliance.

The point of origin and the termination of the raceway shall be labeled, “For future heat pump space heating equipment.”

**C405.17.2 Water heating.** Locations with piping for fossil fuel water heaters shall comply with Section C405.17.2.1 or C405.17.2.2, as applicable.

**C405.17.2.1 Low-capacity water heating**. Locations of fossil fuel water heaters with an input rating of less than 300,000 Btu/hr (88 kW) shall comply with all of the following:

1. An individual 30-ampere, 208/240-volt branch circuit shall be provided and terminate within 6 feet (1829 mm) of the water heater and shall be in a location with ready access.
2. The branch circuit overcurrent protection device and the termination of the branch circuit shall be labeled, “For future electric water heater.”
3. The space for containing the future water heater shall have a height of not less than 7 feet (2134 mm), a width of not less than 3 feet (914 mm), a depth of not less than 3 feet (914 mm) and with a volume of not less than 700 cubic feet (20 m3).

**Exception:** Where the space containing the water heater provides for air circulation sufficient for the operation of a heat pump water heater, the minimum room volume shall not be required.

**C405.17.2.2 Other water heating.** Locations of fossil fuel water-heating equipment not covered by Section C405.17.2.1 shall be provided with a raceway in accordance with all of the following:

1. The raceway shall be continuous from an electric panel to a junction box located within the same space as the equipment or, where the equipment is located on the exterior of the building, within 3 feet (914 mm) of the equipment.
2. The junction box, raceway and bus bar in the electric panel and conductors serving the electric panel shall be sized to accommodate electric water-heating equipment sized to serve the same load as the fossil fuel water-heating equipment.
3. The electric panel shall have sufficient reserved physical space for branch circuit overprotection devices sized to serve electric water-heating equipment sized to serve the same load as the fossil fuel water-heating equipment.
4. The point of origin and termination of the raceway shall be labeled, “For future electric water heating appliance.”

**C405.17.3 Noncommercial cooking.** Locations of fossil fuel ranges, cooktops and ovens that are not commercial cooking

appliances shall be provided with a dedicated individual branch circuit in accordance with all of the following:

1. The branch circuit shall be rated for 208/240 volts and not less than 50 amps.
2. The branch circuit shall terminate within 3 feet (914 mm) of the appliance and shall be in a location with ready access.
3. The point of origin and termination of the branch circuit shall be labeled, “For future electric cooking appliance.”

**C405.17.4 Clothes drying.** Locations with piping for fossil fuel clothes-drying equipment shall comply with Section

C405.17.4.1 or C405.17.4.2, as applicable.

**C405.17.4.1 Residential drying.** Locations of fossil fuel clothes-drying appliances serving individual dwellings units shall be provided with a dedicated individual branch circuit in accordance with all of the following:

1. The branch circuit shall be rated for 208/240 volts and not less than 30 amps.
2. The branch circuit shall terminate within 3 feet (914 mm) of the appliance and shall be in a location with ready access.
3. The point of origin and termination of the branch circuit shall be labeled, “For future electric clothes-drying appliance.”

**C405.17.4.2 Nonresidential drying.** Locations of fossil fuel clothes-drying appliances not covered by Section C405.17.4.1 shall be provided with a raceway in accordance with all of the following:

The raceway shall be continuous from an electric panel to a junction box located within the same space a the appliances.

The junction box, raceway and bus bar in the electric panel and conductors serving the electric panel shall be sized to serve electric clothes-drying appliances having the same drying capacity y as the fossil fuel clothes-drying appliances.

The electric panel shall have sufficient reserved physical space for branch circuit overprotection devices sized to serve electric clothes-drying appliances sized to serve the same load as the fossil fuel clothes-drying appliances.

The point of origin and termination of the raceway shall be labeled, “For future electric clothes drying appliance.”

**C405.17.5 On-site transformers.** Enclosed spaces and underground vaults containing on-site electric transformers on the building side of the electric utility meter shall have sufficient space to accommodate transformers sized to serve the additional electric loads identified in SectionsC405.17.1, C405.17.2, C405.17.3 and C405.17.4.

SECTION C406—ADDITIONAL EFFICIENCY, RENEWABLE AND LOAD MANAGEMENT REQUIREMENTS

**C406.1 Compliance.** *Buildings* shall comply as follows:

1. *Buildings* with greater than 2,000 square feet (186 m2) of *conditioned floor are*a shall comply with Section C406.1.1.
2. *Buildings* with greater than 5,000 square feet (465 m2) of *conditioned floor area* shall comply with Sections C406.1.1 and C406.1.2.
3. Build-out construction greater than 1,000 square feet (93 m2) of *conditioned floor area* that does not have final lighting or final HVAC systems installed under a prior building permit shall comply with Section C406.1.1.2.

**Exceptions:** Core and shell *buildings* where not less than 20 percent of the net floor area is without final light- ing or final HVAC that comply with all of the following:

1. *Buildings* with greater than 5,000 square feet (465 m2) of *conditioned floor area* shall comply with Section C406.1.2.
2. Portions of the *building* where the net floor area is without final lighting or final HVAC shall comply with Section C406.1.1.2.
3. Portions of the *building* where the net floor area has final lighting and final HVAC systems shall comply with Section C406.1.1.

**C406.1.1 Additional energy efficiency credit requirements.** *Buildings* shall comply with measures from Section C406.2 to achieve not less than the number of required efficiency credits from Table C406.1.1(1) based on building occupancy group and *climate zone*, including any energy credit adjustments in accordance with Section C406.1.1.1*.* Where a project contains multiple occupancies, the total required energy credits from each building occupancy shall be weighted by the gross *conditioned floor area* to determine the weighted-average project energy credits required. Accessory occupancies shall be included with the primary occupancy group for the purposes of Section C406.

Exceptions:

1. Portions of *buildings* devoted to manufacturing or industrial use.
2. Where a *building* achieves more renewable and load management credits in Section C406.3 than are required in Section C406.1.2, surplus credits shall be permitted to reduce the required energy efficiency credits as follows:

**Equation 4-12** *EECred* = *EECtbl* - {the lesser of: [*SLRMlim*, *SRLMadj* × (*RLMach* - *RLMreq*)]} where:

*EECred* = Reduced required energy efficiency credits.

*EECtbl* = Required energy efficiency credits from Table C406.1.1(1).

*SRLMlim* = Surplus renewable and load management credit limit from Table C406.1.1(2).

*SRLMadj* = 1.0 for all-electric or all-renewable buildings (excluding emergency generation); 0.7 for buildings with fossil fuel equipment (excluding emergency generation).

*RLMach* = Achieved renewable and load management credits from Section C406.3.

*RLMreq* = Required renewable and load management credits from Section C406.1.2.

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE C406.1.1(1)—ENERGY CREDIT REQUIREMENTS BY BUILDING OCCUPANCY GROUP** | | | | | | | | | | | | | | | | | | | |
| **BUILDING OCCUPANCY GROUP** | **CLIMATE ZONE** | | | | | | | | | | | | | | | | | | |
| **0A** | **0B** | **1A** | **1B** | **2A** | **2B** | **3A** | **3B** | **3C** | **4A** | **4B** | **4C** | **5A** | **5B** | **5C** | **6A** | **6B** | **7** | **8** |
| R-2, R-4 and I-1 | 65 | 66 | 67 | 77 | 80 | 86 | 80 | 81 | 90 | 86 | 90 | 90 | 86 | 90 | 90 | 70 | 89 | 80 | 78 |
| I-2 | 43 | 42 | 38 | 37 | 36 | 38 | 32 | 32 | 30 | 36 | 36 | 35 | 43 | 43 | 44 | 46 | 47 | 50 | 53 |
| R-1 | 63 | 62 | 66 | 65 | 70 | 71 | 77 | 80 | 84 | 81 | 83 | 88 | 85 | 86 | 90 | 83 | 87 | 87 | 85 |
| B | 62 | 62 | 64 | 66 | 66 | 65 | 64 | 64 | 68 | 70 | 72 | 74 | 71 | 73 | 77 | 71 | 74 | 74 | 71 |
| A-2 | 70 | 70 | 72 | 72 | 75 | 75 | 70 | 73 | 82 | 69 | 74 | 78 | 67 | 72 | 78 | 60 | 67 | 57 | 51 |
| M | 80 | 79 | 83 | 79 | 81 | 84 | 67 | 74 | 87 | 80 | 66 | 65 | 79 | 62 | 50 | 75 | 67 | 75 | 58 |
| E | 56 | 57 | 55 | 58 | 58 | 57 | 59 | 62 | 59 | 61 | 66 | 62 | 64 | 67 | 67 | 65 | 67 | 63 | 58 |
| S-1 and S-2 | 61 | 60 | 61 | 60 | 58 | 57 | 44 | 54 | 62 | 85 | 68 | 75 | 90 | 82 | 72 | 90 | 89 | 90 | 90 |
| All other | 31 | 31 | 31 | 32 | 32 | 33 | 30 | 32 | 36 | 35 | 35 | 35 | 37 | 36 | 36 | 36 | 37 | 36 | 34 |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE C406.1.1(2)—LIMIT TO ENERGY EFFICIENCY CREDIT CARRYOVER FROM RENEWABLE AND LOAD MANAGEMENT CREDITS** | | | | | | | | | | | | | | | | | | | |
| **BUILDING OCCUPANCY GROUP** | **CLIMATE ZONE** | | | | | | | | | | | | | | | | | | |
| **0A** | **0B** | **1A** | **1B** | **2A** | **2B** | **3A** | **3B** | **3C** | **4A** | **4B** | **4C** | **5A** | **5B** | **5C** | **6A** | **6B** | **7** | **8** |
| R-2, R-4 and I-1 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 24 | 19 | 5 | 22 | 18 | 5 | 5 | 19 | 5 | 5 | 5 | 5 |
| I-2 | 16 | 14 | 11 | 8 | 6 | 5 | 5 | 10 | 6 | 8 | 14 | 10 | 17 | 26 | 29 | 21 | 21 | 22 | 39 |
| R-1 | 7 | 5 | 8 | 5 | 19 | 5 | 32 | 40 | 41 | 24 | 41 | 42 | 17 | 37 | 41 | 5 | 24 | 15 | 22 |
| B | 7 | 5 | 5 | 8 | 6 | 6 | 14 | 26 | 31 | 23 | 39 | 34 | 19 | 35 | 45 | 5 | 19 | 17 | 27 |
| A-2 | 18 | 16 | 14 | 15 | 13 | 9 | 11 | 23 | 32 | 5 | 23 | 23 | 5 | 5 | 26 | 5 | 5 | 5 | 5 |
| M | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 20 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |
| E | 13 | 13 | 18 | 16 | 17 | 14 | 21 | 35 | 40 | 25 | 43 | 29 | 23 | 32 | 27 | 11 | 17 | 25 | 5 |
| S-1 and S-2 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 13 | 5 | 17 | 20 | 5 | 35 | 23 | 5 | 5 | 11 | 40 |
| All other | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 7 | 17 | 5 | 10 | 7 | 5 | 6 | 11 | 5 | 5 | 5 | 5 |

C406.1.1.1 ~~Reserved.~~ Buildings without heat pumps. The number of efficiency credits required by Section C406.1.1 shall be multiplied by 1.25 for the following:

1. Buildings use purchased energy that is not electricity for space heating or service water heating.
2. Buildings with electric storage water heaters that are not heat pumps.
3. Buildings with total heat pump space heating capacity less than the space heating load at heating design conditions calculated in accordance with Section C403.1.1.

Exceptions:

1. Portions of buildings devoted to manufacturing or industrial use.
2. Buildings complying with all of the following:
   1. The building’s peak heating load calculated in accordance with Section C403.1.1 is greater than the building’s

peak cooling load calculated in accordance with Section C403.1.1.

* 1. The building’s total heat pump space heating capacity is not less than 50 percent of the building’s space heating load at heating design conditions calculated in accordance with Section C403.1.1.
  2. Any energy source other than electricity or on-site renewable energy is used for space heating only when a heat pump cannot provide the necessary heating energy to satisfy the thermostat setting.
  3. Electric resistance heat is used only in accordance with Section C403.4.1.1.

1. Low-energy buildings complying with Section C402.1.1.1.
2. Portions of buildings in Utility and Miscellaneous Group U, Storage Group S, Factory Group F or High-Hazard Group H.
3. Buildings located in Climate Zones 0A, 0B, 1A, 1B, 2A and 2B.

**C406.1.1.2 Building core/shell and build-out construction.** Where separate permits are issued for core and shell *buildings*

and build-out construction, compliance shall be in accordance with the following requirements.

* 1. Core and shell *buildings* or portions of *buildings* shall comply with one of the following:
     1. Where the permit includes a central HVAC system or *service water heating* system with chillers, heat pumps, boilers, *service water heating* equipment or loop pumping systems with heat rejection, the project shall achieve not less than 50 percent of the energy credits required by Section C406.1.1 and C406.1.1.1 in accordance with Section C406.2.
     2. Alternatively, the project shall achieve not less than 33 percent of the energy credits required by Section C406.1.1 and C406.1.1.1.
  2. For core and shell buildings or portions of *buildings*, the energy credits achieved shall be subject to the following adjustments:
     1. Lighting measure credits shall be determined only for areas with final lighting installed.
     2. Where HVAC or *service water heating* systems are designed to serve the entire *building*, full HVAC or *service water heating* measure credits shall be achieved.
     3. Where HVAC or *service water heating* systems are designed to serve individual areas, HVAC or *service water heating* measure credits achieved shall be reduced in proportion to the floor area with final HVAC systems or final *service water heating* systems installed.

1. Build-out construction shall be deemed to comply with Section C406.1 where one of the following applies:
   * 1. Where heating and cooling generation is provided by a previously installed central system, the energy cred- its achieved in accordance with Section C406.2 under the build-out project are not less than 33 percent of the credits required by Section C406.1.1 and C406.1.1.1.
     2. Where heating and cooling generation is provided by an HVAC system installed in the build-out, the energy credits achieved in accordance with Section C406.2 under the build-out project are not less than 50 percent of the credits required by Section C406.1.1 and C406.1.1.1.
     3. Where the core and shell *building* is *approved* in accordance with Section C407 under the 2021 IECC or later.

**C406.1.2 Additional renewable and load management credit requirements.** *Buildings* shall comply with measures from Section C406.3 to achieve not less than the number of required renewable and load management credits from Table C406.1.2 based on building occupancy group and *climate zone*. Where a project contains multiple occupancies, credits in Table C406.1.2 from each building occupancy shall be weighted by the gross floor area to determine the weighted-average project energy credits required. Accessory occupancies shall be included with the primary occupancy group for the purposes of Section C406.

**Exception:** Where a *building* achieves more energy efficiency credits in Section C406.2 than are required in Section C406.1.1, the renewable and load management credits required in Table C406.1.2 shall be permitted to be reduced by the amount of surplus energy efficiency credits.

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE C406.1.2—RENEWABLE AND LOAD MANAGEMENT CREDIT REQUIREMENTS BY BUILDING OCCUPANCY GROUP** | | | | | | | | | | | | | | | | | | | |
| **BUILDING OCCUPANCY GROUP** | **CLIMATE ZONE** | | | | | | | | | | | | | | | | | | |
| **0A** | **0B** | **1A** | **1B** | **2A** | **2B** | **3A** | **3B** | **3C** | **4A** | **4B** | **4C** | **5A** | **5B** | **5C** | **6A** | **6B** | **7** | **8** |
| R-2, R-4 and I-1 | 34 | 37 | 31 | 46 | 48 | 56 | 49 | 56 | 38 | 31 | 42 | 32 | 26 | 33 | 34 | 23 | 27 | 25 | 25 |
| I-2 | 23 | 24 | 25 | 25 | 25 | 28 | 26 | 30 | 22 | 25 | 32 | 24 | 25 | 28 | 29 | 26 | 28 | 22 | 20 |
| R-1 | 30 | 28 | 35 | 30 | 34 | 36 | 34 | 37 | 41 | 32 | 37 | 27 | 28 | 33 | 32 | 25 | 29 | 22 | 18 |
| B | 38 | 39 | 45 | 42 | 45 | 49 | 47 | 56 | 57 | 44 | 55 | 42 | 38 | 47 | 46 | 38 | 45 | 38 | 31 |
| A-2 | 8 | 8 | 9 | 9 | 8 | 9 | 9 | 11 | 13 | 8 | 11 | 9 | 8 | 10 | 9 | 8 | 9 | 8 | 3 |
| M | 32 | 32 | 42 | 37 | 39 | 47 | 44 | 58 | 57 | 42 | 54 | 46 | 38 | 48 | 5 | 42 | 45 | 38 | 34 |
| E | 27 | 34 | 38 | 37 | 39 | 47 | 44 | 58 | 57 | 42 | 54 | 46 | 38 | 48 | 50 | 42 | 45 | 38 | 34 |
| S-1 and S-2 | 89 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 70 | 90 | 90 | 84 | 86 | 71 | 54 |
| All other | 35 | 39 | 46 | 42 | 46 | 52 | 49 | 56 | 56 | 40 | 52 | 42 | 37 | 44 | 44 | 36 | 39 | 32 | 28 |

**C406.2 Additional energy efficiency credits achieved.** Each energy efficiency credit measure used to meet credit requirements for the project shall have efficiency that is greater than the requirements in Sections C402 through C405. Measures installed in the proj- ect that meet the requirements in Sections C406.2.1 through C406.2.6 shall achieve the base credits listed for the measure and occupancy type in Tables C406.2(1) through C406.2(9) or, where calculations required by Sections C406.2.1 through C406.2.6 create or modify the table credits, the credits achieved shall be based on the calculations. Energy credits achieved for measures shall be determined by one of the following, as applicable:

1. The measure’s energy credit shall be the base energy credit from Tables C406.2(1) through C406.2(9) for the measure where no adjustment factor or calculation is included in the description of the measure in Section C406.2.
2. The measure’s energy credit shall be the base energy credit for the measure adjusted by a factor or equation as stated in the description of the measure in Section C406.2. Where adjustments are applied, each measure’s energy credit shall be rounded to the nearest whole number.
3. The measure’s energy credit shall be calculated as stated in the measure’s description in Section C406.2, where each indi- vidual measure credit shall be rounded to the nearest whole number.

Energy credits achieved for the project shall be the sum of the individual measure’s energy credits. Credits are available for the measures listed in this section. Where a project contains multiple building occupancy groups:

1. Credits achieved for each occupancy group shall be summed and then weighted by the *conditioned floor area* of each occu- pancy group to determine the weighted average project energy credits achieved.
2. Improved envelope efficiency (E01 through E06), HVAC performance (H01) and lighting reduction (L06) measure credits shall be determined for the *building* or permitted *conditioned floor area* as a whole. Credits for other measures shall be determined for each occupancy separately. Credits shall be taken from applicable tables or calculations for each occu- pancy and weighted by the building occupancy group floor area.

**COMMERCIAL ENERGY EFFICIENCY**

**2024 INTERNATIONAL ENERGY CONSERVATION CODE®**

**163**

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE C406.2(1)—BASE ENERGY CREDITS FOR GROUP R-2, R-4 AND I-1 OCCUPANCIESa** | | | | | | | | | | | | | | | | | | | | | |
| **ID** | **ENERGY CREDIT MEASURE** | **SECTION** | **CLIMATE ZONE** | | | | | | | | | | | | | | | | | | |
| **0A** | **0B** | **1A** | **1B** | **2A** | **2B** | **3A** | **3B** | **3C** | **4A** | **4B** | **4C** | **5A** | **5B** | **5C** | **6A** | **6B** | **7** | **8** |
| E01 | Envelope performance | C406.2.1.1 | Determined in accordance with Section C406.2.1.1 | | | | | | | | | | | | | | | | | | |
| E02 | UA reduction (15%) | C406.2.1.2 | 7 | 6 | 2 | 4 | 1 | 1 | 4 | 1 | 1 | 22 | 1 | 3 | 29 | 10 | 1 | 32 | 27 | 30 | 39 |
| E03 | Reduced air leakage | C406.2.1.3 | 15 | 10 | 12 | 8 | 6 | 16 | 13 | 5 | 1 | 7 | 7 | 9 | 65 | 16 | 11 | 73 | 43 | 52 | 26 |
| E04 | Add roof insulation | C406.2.1.4 | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 3 | 1 | 5 | 3 | 4 | 6 | 5 | 4 | 7 | 7 | 6 | 8 |
| E05 | Add wall insulation | C406.2.1.5 | 10 | 10 | 6 | 8 | 5 | 6 | 8 | 4 | 1 | 8 | 3 | 4 | 11 | 7 | 3 | 14 | 12 | 13 | 13 |
| E06 | Improve fenestration | C406.2.1.6 | 7 | 7 | 4 | 6 | 9 | 11 | 13 | 3 | 1 | 22 | 5 | 10 | 27 | 18 | 7 | 41 | 33 | 22 | 21 |
| H01 | HVAC performance | C406.2.2.1 | 20 | 19 | 16 | 17 | 14 | 13 | 11 | 11 | 5 | 13 | 10 | 8 | 15 | 12 | 7 | 18 | 14 | 17 | 19 |
| H02 | Heating efficiency | C406.2.2.2 | x | x | x | x | x | x | 3 | 1 | 1 | 6 | 2 | 3 | 10 | 5 | 2 | 14 | 10 | 13 | 16 |
| H03 | Cooling efficiency | C406.2.2.3 | 7 | 6 | 4 | 4 | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | x | x | x | x | x |
| H04 | Residential HVAC control | C406.2.2.4 | 9 | 10 | 8 | 22 | 20 | 25 | 16 | 17 | 32 | 21 | 24 | 17 | 23 | 27 | 16 | 21 | 24 | 18 | 18 |
| H05 | DOAS/fan control | C406.2.2.5 | 32 | 31 | 27 | 28 | 23 | 23 | 28 | 21 | 12 | 42 | 24 | 24 | 56 | 36 | 19 | 73 | 54 | 70 | 79 |
| W01 | SHW preheat recovery | C406.2.3.1 a | 61 | 63 | 74 | 74 | 85 | 88 | 101 | 100 | 121 | 103 | 109 | 122 | 102 | 111 | 130 | 93 | 106 | 99 | 96 |
| W02 | Heat pump water heater | C406.2.3.1 b | 50 | 52 | 62 | 61 | 72 | 74 | 86 | 85 | 104 | 88 | 94 | 106 | 88 | 96 | 112 | 81 | 92 | 87 | 84 |
| W03 | Efficient gas water heater | C406.2.3.1 c | 38 | 39 | 46 | 46 | 53 | 55 | 63 | 62 | 76 | 64 | 68 | 76 | 64 | 69 | 81 | 58 | 66 | 62 | 60 |
| W04 | SHW pipe insulation | C406.2.3.2 | 7 | 7 | 8 | 7 | 8 | 8 | 8 | 9 | 10 | 8 | 9 | 9 | 7 | 8 | 9 | 6 | 7 | 6 | 6 |
| W05 | Point of use water heaters | C406.2.3.3 a | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| W06 | Thermostatic bal. valves | C406.2.3.3 b | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 3 | 3 | 4 | 3 | 3 | 4 | 3 | 3 | 3 | 2 |
| W07 | SHW heat trace system | C406.2.3.3 c | 12 | 12 | 13 | 13 | 14 | 15 | 15 | 15 | 18 | 14 | 15 | 16 | 13 | 14 | 16 | 11 | 13 | 11 | 10 |
| W08 | SHW submeters | C406.2.3.4 | 11 | 11 | 13 | 13 | 15 | 16 | 18 | 18 | 22 | 19 | 20 | 22 | 19 | 20 | 24 | 17 | 20 | 18 | 18 |
| W09 | SHW flow reduction | C406.2.3.5 | 22 | 22 | 27 | 26 | 31 | 32 | 37 | 37 | 45 | 38 | 40 | 45 | 38 | 41 | 48 | 35 | 39 | 37 | 36 |
| W10 | Shower heat recovery | C406.2.3.6 | 15 | 16 | 19 | 19 | 22 | 23 | 26 | 26 | 32 | 27 | 29 | 32 | 27 | 29 | 34 | 25 | 28 | 27 | 26 |
| P01 | Energy monitoring | C406.2.4 | 3 | 3 | 2 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 2 | 2 | 3 |
| L01 | Lighting performance | C406.2.5.1 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| L02 | Lighting dimming & tuning | C406.2.5.2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |
| L03 | Increase occp. sensor | C406.2.5.3 | 3 | 3 | 4 | 4 | 4 | 4 | 3 | 4 | 3 | 2 | 3 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 1 |
| L04 | Increase daylight area | C406.2.5.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| L05 | Residential light control | C406.2.5.5 | 8 | 8 | 9 | 9 | 9 | 9 | 8 | 8 | 10 | 6 | 8 | 7 | 4 | 6 | 8 | 3 | 5 | 4 | 3 |
| L06 | Light power reduction | C406.2.5.6 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |
| Q01 | Efficient elevator | C406.2.6.1 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 4 | 5 | 5 | 4 | 4 | 5 | 4 | 4 | 4 | 3 |
| Q02 | Commercial kitchen equip. | C406.2.6.2 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| Q03 | Residential kitchen equip. | C406.2.6.3 | 15 | 15 | 17 | 16 | 17 | 18 | 17 | 18 | 20 | 16 | 17 | 18 | 15 | 16 | 18 | 13 | 15 | 13 | 12 |
| Q04 | Fault detection | C406.2.6.4 | 3 | 3 | 2 | 3 | 2 | 2 | 2 | 2 | 1 | 2 | 2 | 1 | 1 | 2 | 1 | 3 | 2 | 3 | 3 |
| DOAS = Dedicated Outside Air System; HVAC = Heating, Ventilation and Air Conditioning; SHW = Service Hot Water; UA = *U*-factor × Area.  a. “x” indicates credit is not available in that climate zone for that measure. | | | | | | | | | | | | | | | | | | | | | |

**COMMERCIAL ENERGY EFFICIENCY**

**164**

**2024 INTERNATIONAL ENERGY CONSERVATION CODE®**

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE C406.2(2)—BASE ENERGY CREDITS FOR GROUP I-2 OCCUPANCIESa** | | | | | | | | | | | | | | | | | | | | | |
| **ID** | **ENERGY CREDIT MEASURE** | **SECTION** | **CLIMATE ZONE** | | | | | | | | | | | | | | | | | | |
| **0A** | **0B** | **1A** | **1B** | **2A** | **2B** | **3A** | **3B** | **3C** | **4A** | **4B** | **4C** | **5A** | **5B** | **5C** | **6A** | **6B** | **7** | **8** |
| E01 | Envelope performance | C406.2.1.1 | Determined in accordance with Section C406.2.1.1 | | | | | | | | | | | | | | | | | | |
| E02 | UA reduction (15%) | C406.2.1.2 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 3 | 1 | 3 | 11 | 27 | 7 | 10 | 3 | 3 | 2 | 10 |
| E03 | Reduced air leakage | C406.2.1.3 | 5 | 3 | 4 | 3 | 5 | 8 | 8 | 3 | 2 | 6 | 2 | 2 | 7 | 3 | 1 | 9 | 7 | 19 | 5 |
| E04 | Add roof insulation | C406.2.1.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 2 | 1 | 2 | 3 |
| E05 | Add wall insulation | C406.2.1.5 | 1 | 3 | 1 | 3 | 2 | 2 | 9 | 4 | 1 | 4 | 1 | 1 | 3 | 1 | 1 | 3 | 3 | 3 | 3 |
| E06 | Improve fenestration | C406.2.1.6 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 3 | 5 | 5 | 1 | 1 | 5 | 5 | 2 | 2 |
| H01 | HVAC performance | C406.2.2.1 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| H02 | Heating efficiency | C406.2.2.2 | x | x | x | x | 2 | 3 | 4 | 3 | 7 | 6 | 4 | 6 | 8 | 6 | 10 | 11 | 12 | 15 | 19 |
| H03 | Cooling efficiency | C406.2.2.3 | 6 | 6 | 4 | 4 | 3 | 3 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | x | x | x | x |
| H04 | Residential HVAC control | C406.2.2.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| H05 | DOAS/fan control | C406.2.2.5 | 41 | 41 | 40 | 40 | 42 | 36 | 42 | 37 | 39 | 49 | 40 | 46 | 56 | 46 | 61 | 65 | 68 | 82 | 93 |
| W01 | SHW preheat recovery | C406.2.3.1 a | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 5 | 5 | 5 |
| W02 | Heat pump water heater | C406.2.3.1 b | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |
| W03 | Efficient gas water heater | C406.2.3.1 c | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |
| W04 | SHW pipe insulation | C406.2.3.2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |
| W05 | Point of use water heaters | C406.2.3.3 a | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| W06 | Thermostatic bal. valves | C406.2.3.3 b | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |
| W07 | SHW heat trace system | C406.2.3.3 c | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 |
| W08 | SHW submeters | C406.2.3.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| W09 | SHW flow reduction | C406.2.3.5 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| W10 | Shower heat recovery | C406.2.3.6 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |
| P01 | Energy monitoring | C406.2.4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |
| L01 | Lighting performance | C406.2.5.1 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| L02 | Lighting dimming & tuning | C406.2.5.2 | 5 | 5 | 5 | 5 | 5 | 6 | 5 | 6 | 6 | 5 | 6 | 6 | 5 | 5 | 5 | 4 | 4 | 3 | 2 |
| L03 | Increase occp. sensor | C406.2.5.3 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 5 | 5 | 6 | 5 | 5 | 5 | 4 | 4 | 3 | 2 |
| L04 | Increase daylight area | C406.2.5.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| L05 | Residential light control | C406.2.5.5 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| L06 | Light power reduction | C406.2.5.6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 9 | 7 | 7 | 8 | 6 | 7 | 7 | 5 | 5 | 4 | 3 |
| Q01 | Efficient elevator | C406.2.6.1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 |
| Q02 | Commercial kitchen equip. | C406.2.6.2 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| Q03 | Residential kitchen equip. | C406.2.6.3 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| Q04 | Fault detection | C406.2.6.4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 3 | 3 | 2 | 3 | 3 | 3 | 3 | 3 | 4 | 4 |
| DOAS = Dedicated Outside Air System; HVAC = Heating, Ventilation and Air Conditioning; SHW = Service Hot Water; UA = *U*-Factor × Area.  a. “x” indicates credit is not available in that climate zone for that measure. | | | | | | | | | | | | | | | | | | | | | |

**COMMERCIAL ENERGY EFFICIENCY**

**2024 INTERNATIONAL ENERGY CONSERVATION CODE®**

**165**

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE C406.2(3)—BASE ENERGY CREDITS FOR GROUP R-1 OCCUPANCIESa** | | | | | | | | | | | | | | | | | | | | | |
| **ID** | **ENERGY CREDIT MEASURE** | **SECTION** | **CLIMATE ZONE** | | | | | | | | | | | | | | | | | | |
| **0A** | **0B** | **1A** | **1B** | **2A** | **2B** | **3A** | **3B** | **3C** | **4A** | **4B** | **4C** | **5A** | **5B** | **5C** | **6A** | **6B** | **7** | **8** |
| E01 | Envelope performance | C406.2.1.1 | Determined in accordance with Section C406.2.1.1 | | | | | | | | | | | | | | | | | | |
| E02 | UA reduction (15%) | C406.2.1.2 | 2 | 3 | 1 | 2 | 1 | 3 | 3 | 2 | 1 | 5 | 2 | 2 | 7 | 4 | 2 | 9 | 7 | 9 | 11 |
| E03 | Reduced air leakage | C406.2.1.3 | 15 | 9 | 12 | 8 | 6 | 16 | 7 | 5 | 10 | 14 | 3 | 1 | 19 | 5 | 1 | 28 | 16 | 28 | 18 |
| E04 | Add roof insulation | C406.2.1.4 | 1 | 1 | 1 | 2 | 2 | 1 | 2 | 1 | 1 | 2 | 1 | 2 | 2 | 1 | 2 | 3 | 2 | 2 | 3 |
| E05 | Add wall insulation | C406.2.1.5 | 18 | 26 | 11 | 25 | 3 | 4 | 5 | 3 | 1 | 6 | 2 | 4 | 7 | 4 | 4 | 8 | 6 | 8 | 5 |
| E06 | Improve fenestration | C406.2.1.6 | 2 | 2 | 1 | 2 | 2 | 3 | 5 | 3 | 1 | 6 | 3 | 4 | 9 | 7 | 6 | 13 | 8 | 6 | 6 |
| H01 | HVAC performance | C406.2.2.1 | 21 | 20 | 17 | 18 | 16 | 13 | 12 | 12 | 11 | 11 | 11 | 8 | 11 | 11 | 8 | 13 | 11 | 14 | 16 |
| H02 | Heating efficiency | C406.2.2.2 | x | x | x | x | x | x | 1 | 1 | 6 | 2 | 1 | 1 | 3 | 2 | 2 | 6 | 4 | 8 | 11 |
| H03 | Cooling efficiency | C406.2.2.3 | 7 | 6 | 4 | 4 | 3 | 2 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | x | x | x | x |
| H04 | Residential HVAC control | C406.2.2.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| H05 | DOAS/fan control | C406.2.2.5 | 32 | 30 | 26 | 28 | 25 | 23 | 24 | 22 | 28 | 26 | 22 | 20 | 30 | 26 | 19 | 41 | 34 | 48 | 62 |
| W01 | SHW preheat recovery | C406.2.3.1 a | 18 | 19 | 22 | 22 | 25 | 27 | 31 | 21 | 32 | 34 | 34 | 38 | 37 | 36 | 40 | 36 | 37 | 36 | 35 |
| W02 | Heat pump water heater | C406.2.3.1 b | 14 | 15 | 18 | 17 | 20 | 22 | 25 | 25 | 27 | 29 | 29 | 32 | 31 | 31 | 34 | 30 | 32 | 31 | 30 |
| W03 | Efficient gas water heater | C406.2.3.1 c | 11 | 12 | 14 | 14 | 16 | 17 | 19 | 19 | 20 | 21 | 21 | 24 | 23 | 23 | 25 | 22 | 23 | 23 | 22 |
| W04 | SHW pipe insulation | C406.2.3.2 | 3 | 3 | 4 | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 3 |
| W05 | Point of use water heaters | C406.2.3.3 a | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| W06 | Thermostatic bal. valves | C406.2.3.3 b | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 |
| W07 | SHW heat trace system | C406.2.3.3 c | 5 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 7 | 8 | 7 | 7 | 6 | 6 |
| W08 | SHW submeters | C406.2.3.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| W09 | SHW flow reduction | C406.2.3.5 | 6 | 7 | 8 | 8 | 9 | 10 | 11 | 11 | 12 | 13 | 13 | 14 | 14 | 13 | 15 | 13 | 14 | 14 | 13 |
| W10 | Shower heat recovery | C406.2.3.6 | 4 | 5 | 5 | 5 | 6 | 7 | 8 | 8 | 8 | 9 | 9 | 10 | 10 | 9 | 10 | 9 | 10 | 10 | 9 |
| P01 | Energy monitoring | C406.2.4 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |
| L01 | Lighting performance | C406.2.5.1 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| L02 | Lighting dimming & tuning | C406.2.5.2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |
| L03 | Increase occp. sensor | C406.2.5.3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 2 | 3 | 2 | 2 | 3 | 2 | 2 | 1 | 1 |
| L04 | Increase daylight area | C406.2.5.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| L05 | Residential light control | C406.2.5.5 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| L06 | Light power reduction | C406.2.5.6 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 1 |
| Q01 | Efficient elevator | C406.2.6.1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 |
| Q02 | Commercial kitchen equip. | C406.2.6.2 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| Q03 | Residential kitchen equip. | C406.2.6.3 | 9 | 9 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 11 | 11 | 12 | 10 | 11 | 10 | 9 |
| Q04 | Fault detection | C406.2.6.4 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 2 | 2 | 2 | 2 |
| DOAS = Dedicated Outside Air System; HVAC = Heating, Ventilation and Air Conditioning; SHW = Service Hot Water; UA = *U*-Factor × Area.  a. “x” indicates credit is not available in that climate zone for that measure. | | | | | | | | | | | | | | | | | | | | | |

**COMMERCIAL ENERGY EFFICIENCY**

**166**

**2024 INTERNATIONAL ENERGY CONSERVATION CODE®**

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE C406.2(4)—BASE ENERGY CREDITS FOR GROUP B OCCUPANCIESa** | | | | | | | | | | | | | | | | | | | | | |
| **ID** | **ENERGY CREDIT MEASURE** | **SECTION** | **CLIMATE ZONE** | | | | | | | | | | | | | | | | | | |
| **0A** | **0B** | **1A** | **1B** | **2A** | **2B** | **3A** | **3B** | **3C** | **4A** | **4B** | **4C** | **5A** | **5B** | **5C** | **6A** | **6B** | **7** | **8** |
| E01 | Envelope performance | C406.2.1.1 | Determined in accordance with Section C406.2.1.1 | | | | | | | | | | | | | | | | | | |
| E02 | UA reduction (15%) | C406.2.1.2 | 7 | 8 | 3 | 6 | 5 | 3 | 7 | 3 | 1 | 13 | 4 | 8 | 21 | 15 | 11 | 13 | 24 | 37 | 43 |
| E03 | Reduced air leakage | C406.2.1.3 | 5 | 3 | 4 | 2 | 2 | 2 | 5 | 1 | x | 8 | x | 2 | 13 | 4 | x | 18 | 9 | 18 | 7 |
| E04 | Add roof insulation | C406.2.1.4 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 2 | 1 | 3 | 1 | 2 | 3 | 2 | 2 | 3 | 3 | 2 | 3 |
| E05 | Add wall insulation | C406.2.1.5 | 13 | 14 | 8 | 11 | 4 | 4 | 7 | 4 | 1 | 5 | 2 | 4 | 6 | 4 | 3 | 9 | 7 | 10 | 8 |
| E06 | Improve fenestration | C406.2.1.6 | 5 | 5 | 4 | 5 | 7 | 7 | 8 | 2 | 1 | 8 | 2 | 4 | 10 | 5 | 1 | 21 | 17 | 10 | 9 |
| H01 | HVAC performance | C406.2.2.1 | 22 | 22 | 19 | 20 | 17 | 17 | 15 | 15 | 11 | 15 | 15 | 11 | 16 | 15 | 11 | 19 | 17 | 18 | 20 |
| H02 | Heating efficiency | C406.2.2.2 | X | x | x | x | x | x | 1 | 1 | 1 | 3 | 2 | 2 | 5 | 4 | 3 | 9 | 7 | 8 | 12 |
| H03 | Cooling efficiency | C406.2.2.3 | 7 | 6 | 4 | 5 | 3 | 3 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | x | x | x | x |
| H04 | Residential HVAC control | C406.2.2.4 | X | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| H05 | DOAS/fan control | C406.2.2.5 | 31 | 31 | 27 | 29 | 25 | 25 | 28 | 26 | 18 | 35 | 28 | 28 | 47 | 38 | 29 | 64 | 53 | 58 | 74 |
| W01 | SHW preheat recovery | C406.2.3.1 a | 8 | 9 | 10 | 9 | 11 | 11 | 12 | 12 | 14 | 13 | 13 | 14 | 13 | 13 | 15 | 12 | 13 | 14 | 14 |
| W02 | Heat pump water heater | C406.2.3.1 b | 3 | 3 | 3 | 3 | 4 | 4 | 5 | 4 | 5 | 5 | 5 | 6 | 5 | 5 | 6 | 5 | 5 | 6 | 6 |
| W03 | Efficient gas water heater | C406.2.3.1 c | 5 | 5 | 6 | 6 | 7 | 7 | 8 | 7 | 8 | 8 | 8 | 9 | 8 | 8 | 9 | 8 | 8 | 9 | 8 |
| W04 | SHW pipe insulation | C406.2.3.2 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 4 | 4 | 5 | 4 | 4 | 5 | 4 | 4 | 4 | 4 |
| W05 | Point of use water heaters | C406.2.3.3 a | 12 | 15 | 17 | 16 | 18 | 18 | 19 | 19 | 22 | 20 | 20 | 22 | 20 | 20 | 22 | 18 | 19 | 20 | 19 |
| W06 | Thermostatic bal. valves | C406.2.3.3 b | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |
| W07 | SHW heat trace system | C406.2.3.3 c | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 6 | 5 | 5 | 6 | 5 | 5 | 6 | 5 | 5 | 5 | 5 |
| W08 | SHW submeters | C406.2.3.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| W09 | SHW flow reduction | C406.2.3.5 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| W10 | Shower heat recovery | C406.2.3.6 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| P01 | Energy monitoring | C406.2.4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |
| L01 | Lighting performance | C406.2.5.1 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| L02 | Lighting dimming & tuning | C406.2.5.2 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 6 | 6 | 6 | 5 | 5 | 6 | 4 | 5 | 3 | 2 |
| L03 | Increase occp. sensor | C406.2.5.3 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 8 | 6 | 6 | 6 | 5 | 5 | 6 | 4 | 5 | 4 | 3 |
| L04 | Increase daylight area | C406.2.5.4 | 7 | 7 | 8 | 8 | 8 | 8 | 8 | 8 | 9 | 6 | 7 | 7 | 6 | 6 | 6 | 6 | 6 | 7 | 5 |
| L05 | Residential light control | C406.2.5.5 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| L06 | Light power reduction | C406.2.5.6 | 7 | 7 | 8 | 8 | 8 | 8 | 8 | 8 | 9 | 7 | 8 | 8 | 6 | 7 | 8 | 5 | 6 | 5 | 3 |
| Q01 | Efficient elevator | C406.2.6.1 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 5 | 4 | 4 |
| Q02 | Commercial kitchen equip. | C406.2.6.2 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| Q03 | Residential kitchen equip. | C406.2.6.3 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| Q04 | Fault detection | C406.2.6.4 | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 |
| DOAS = Dedicated Outside Air System; HVAC = Heating, Ventilation and Air Conditioning; SHW = Service Hot Water; UA = *U*-Factor × Area.  a. “x” indicates credit is not available in that climate zone for that measure. | | | | | | | | | | | | | | | | | | | | | |

**COMMERCIAL ENERGY EFFICIENCY**

**2024 INTERNATIONAL ENERGY CONSERVATION CODE®**

**167**

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE C406.2(5)—BASE ENERGY CREDITS FOR GROUP A-2 OCCUPANCIESa** | | | | | | | | | | | | | | | | | | | | | |
| **ID** | **ENERGY CREDIT MEASURE** | **SECTION** | **CLIMATE ZONE** | | | | | | | | | | | | | | | | | | |
| **0A** | **0B** | **1A** | **1B** | **2A** | **2B** | **3A** | **3B** | **3C** | **4A** | **4B** | **4C** | **5A** | **5B** | **5C** | **6A** | **6B** | **7** | **8** |
| E01 | Envelope performance | C406.2.1.1 | Determined in accordance with Section C406.2.1.1 | | | | | | | | | | | | | | | | | | |
| E02 | UA reduction (15%) | C406.2.1.2 | 1 | 1 | 1 | 1 | 13 | 1 | 3 | 2 | 1 | 4 | 4 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 |
| E03 | Reduced air leakage | C406.2.1.3 | 2 | 1 | 1 | 1 | 2 | 3 | 11 | 2 | 1 | 24 | 4 | 6 | 33 | 9 | 3 | 42 | 29 | 36 | 16 |
| E04 | Add roof insulation | C406.2.1.4 | 1 | 1 | x | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 2 | 2 | 1 | 2 |
| E05 | Add wall insulation | C406.2.1.5 | 1 | 1 | x | 1 | 1 | 2 | 3 | 3 | 1 | 2 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |
| E06 | Improve fenestration | C406.2.1.6 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 2 | 2 | 3 | 2 | 1 | 4 | 4 | 1 | 1 |
| H01 | HVAC performance | C406.2.2.1 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| H02 | Heating efficiency | C406.2.2.2 | x | x | x | x | 1 | 1 | 6 | 3 | 3 | 10 | 6 | 8 | 15 | 11 | 10 | 19 | 15 | 23 | 28 |
| H03 | Cooling efficiency | C406.2.2.3 | 6 | 5 | 3 | 4 | 3 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | x | x | x | x |
| H04 | Residential HVAC control | C406.2.2.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| H05 | DOAS/fan control | C406.2.2.5 | 29 | 27 | 20 | 25 | 24 | 21 | 36 | 27 | 15 | 51 | 35 | 38 | 67 | 53 | 45 | 84 | 70 | 97 | 115 |
| W01 | SHW preheat recovery | C406.2.3.1 a | 24 | 26 | 31 | 29 | 33 | 35 | 37 | 38 | 45 | 38 | 41 | 44 | 37 | 40 | 44 | 34 | 38 | 33 | 30 |
| W02 | Heat pump water heater | C406.2.3.1 b | 15 | 16 | 19 | 18 | 21 | 23 | 25 | 25 | 29 | 26 | 28 | 30 | 26 | 28 | 31 | 25 | 27 | 24 | 22 |
| W03 | Efficient gas water heater | C406.2.3.1 c | 15 | 16 | 19 | 18 | 21 | 22 | 23 | 24 | 28 | 24 | 25 | 27 | 23 | 25 | 27 | 21 | 24 | 21 | 18 |
| W04 | SHW pipe insulation | C406.2.3.2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 3 | 3 | 2 | 2 | 2 | 2 |
| W05 | Point of use water heaters | C406.2.3.3 a | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| W06 | Thermostatic bal. valves | C406.2.3.3 b | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |
| W07 | SHW heat trace system | C406.2.3.3 c | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 3 | 4 | 4 | 3 | 3 | 3 | 3 |
| W08 | SHW submeters | C406.2.3.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| W09 | SHW flow reduction | C406.2.3.5 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| W10 | Shower heat recovery | C406.2.3.6 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| P01 | Energy monitoring | C406.2.4 | 2 | 2 | 2 | 2 | 2 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 2 | 2 | 1 | 2 | 2 | 2 | 3 |
| L01 | Lighting performance | C406.2.5.1 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| L02 | Lighting dimming & tuning | C406.2.5.2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 2 | 1 | 1 | 1 | 1 | x |
| L03 | Increase occp. sensor | C406.2.5.3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | x |
| L04 | Increase daylight area | C406.2.5.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| L05 | Residential light control | C406.2.5.5 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| L06 | Light power reduction | C406.2.5.6 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 2 | 1 | 1 |
| Q01 | Efficient elevator | C406.2.6.1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |
| Q02 | Commercial kitchen equip. | C406.2.6.2 | 24 | 26 | 28 | 27 | 28 | 29 | 27 | 29 | 32 | 26 | 28 | 29 | 24 | 26 | 28 | 21 | 23 | 19 | 17 |
| Q03 | Residential kitchen equip. | C406.2.6.3 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| Q04 | Fault detection | C406.2.6.4 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 2 | 2 | 1 | 2 | 2 | 2 | 3 | 2 | 3 | 4 |
| DOAS = Dedicated Outside Air System; HVAC = Heating, Ventilation and Air Conditioning; SHW = Service Hot Water; UA = *U*-Factor × Area.  a. “x” indicates credit is not available in that climate zone for that measure. | | | | | | | | | | | | | | | | | | | | | |

**COMMERCIAL ENERGY EFFICIENCY**

**168**

**2024 INTERNATIONAL ENERGY CONSERVATION CODE®**

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE C406.2(6)—BASE ENERGY CREDITS FOR GROUP M OCCUPANCIESa** | | | | | | | | | | | | | | | | | | | | | |
| **ID** | **ENERGY CREDIT MEASURE** | **SECTION** | **CLIMATE ZONE** | | | | | | | | | | | | | | | | | | |
| **0A** | **0B** | **1A** | **1B** | **2A** | **2B** | **3A** | **3B** | **3C** | **4A** | **4B** | **4C** | **5A** | **5B** | **5C** | **6A** | **6B** | **7** | **8** |
| E01 | Envelope performance | C406.2.1.1 | Determined in accordance with Section C406.2.1.1 | | | | | | | | | | | | | | | | | | |
| E02 | UA reduction (15%) | C406.2.1.2 | 14 | 14 | 8 | 13 | 7 | 9 | 20 | 15 | 1 | 35 | 18 | 28 | 41 | 37 | 40 | 43 | 44 | 46 | 31 |
| E03 | Reduced air leakage | C406.2.1.3 | 3 | 3 | 2 | 2 | 3 | 3 | 19 | 3 | 1 | 44 | 6 | 11 | 56 | 13 | 6 | 64 | 44 | 43 | 19 |
| E04 | Add roof insulation | C406.2.1.4 | 8 | 6 | 5 | 7 | 7 | 7 | 18 | 16 | 4 | 19 | 18 | 20 | 21 | 22 | 23 | 24 | 26 | 24 | 30 |
| E05 | Add wall insulation | C406.2.1.5 | 64 | 65 | 48 | 62 | 13 | 15 | 23 | 18 | 4 | 27 | 21 | 27 | 25 | 24 | 25 | 23 | 24 | 24 | 16 |
| E06 | Improve fenestration | C406.2.1.6 | 4 | 3 | 3 | 3 | 4 | 4 | 6 | 5 | 2 | 7 | 5 | 7 | 7 | 5 | 7 | 10 | 10 | 3 | 3 |
| H01 | HVAC performance | C406.2.2.1 | 31 | 30 | 26 | 28 | 23 | 21 | 23 | 20 | 14 | 27 | 21 | 22 | 29 | 25 | 23 | 32 | 28 | 30 | 33 |
| H02 | Heating efficiency | C406.2.2.2 | x | x | x | x | x | x | 10 | 3 | 1 | 19 | 8 | 15 | 26 | 17 | 18 | 29 | 24 | 27 | 31 |
| H03 | Cooling efficiency | C406.2.2.3 | 10 | 9 | 7 | 7 | 5 | 4 | 2 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | x | x | x | x |
| H04 | Residential HVAC control | C406.2.2.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| H05 | DOAS/fan control | C406.2.2.5 | 48 | 48 | 42 | 47 | 40 | 38 | 66 | 46 | 31 | 98 | 61 | 82 | 120 | 91 | 90 | 134 | 115 | 125 | 141 |
| W01 | SHW preheat recovery | C406.2.3.1 a | 12 | 13 | 16 | 15 | 18 | 20 | 19 | 21 | 26 | 17 | 21 | 21 | 16 | 19 | 21 | 13 | 16 | 15 | 13 |
| W02 | Heat pump water heater | C406.2.3.1 b | 3 | 3 | 4 | 3 | 4 | 5 | 5 | 5 | 7 | 5 | 6 | 6 | 4 | 5 | 6 | 4 | 4 | 4 | 4 |
| W03 | Efficient gas water heater | C406.2.3.1 c | 6 | 7 | 8 | 8 | 10 | 10 | 10 | 11 | 14 | 9 | 11 | 11 | 8 | 10 | 11 | 7 | 8 | 8 | 7 |
| W04 | SHW pipe insulation | C406.2.3.2 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 4 | 4 | 5 | 4 | 4 | 5 | 4 | 4 | 4 | 4 |
| W05 | Point of use water heaters | C406.2.3.3 a | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| W06 | Thermostatic bal. valves | C406.2.3.3 b | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |
| W07 | SHW heat trace system | C406.2.3.3 c | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 6 | 5 | 5 | 6 | 5 | 5 | 6 | 5 | 5 | 5 | 5 |
| W08 | SHW submeters | C406.2.3.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| W09 | SHW flow reduction | C406.2.3.5 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| W10 | Shower heat recovery | C406.2.3.6 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| P01 | Energy monitoring | C406.2.4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |
| L01 | Lighting performance | C406.2.5.1 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| L02 | Lighting dimming & tuning | C406.2.5.2 | 9 | 9 | 11 | 10 | 12 | 13 | 11 | 13 | 15 | 9 | 12 | 11 | 7 | 9 | 10 | 5 | 7 | 5 | 3 |
| L03 | Increase occp. sensor | C406.2.5.3 | 9 | 9 | 11 | 10 | 12 | 13 | 12 | 13 | 15 | 10 | 12 | 11 | 7 | 10 | 11 | 6 | 8 | 5 | 4 |
| L04 | Increase daylight area | C406.2.5.4 | 12 | 13 | 15 | 14 | 16 | 17 | 15 | 16 | 20 | 11 | 14 | 13 | 9 | 12 | 11 | 8 | 10 | 10 | 8 |
| L05 | Residential light control | C406.2.5.5 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| L06 | Light power reduction | C406.2.5.6 | 12 | 12 | 14 | 14 | 15 | 16 | 12 | 15 | 19 | 8 | 12 | 9 | 6 | 10 | 7 | 6 | 7 | 6 | 5 |
| Q01 | Efficient elevator | C406.2.6.1 | 3 | 3 | 4 | 3 | 4 | 4 | 4 | 4 | 5 | 3 | 4 | 4 | 3 | 4 | 4 | 3 | 3 | 3 | 2 |
| Q02 | Commercial kitchen equip. | C406.2.6.2 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| Q03 | Residential kitchen equip. | C406.2.6.3 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| Q04 | Fault detection | C406.2.6.4 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 2 | 2 | 1 | 2 | 2 | 2 | 3 | 2 | 3 | 4 |
| DOAS = Dedicated Outside Air System; HVAC = Heating, Ventilation and Air Conditioning; SHW = Service Hot Water; UA = *U*-Factor × Area.  a. “x” indicates credit is not available in that climate zone for that measure. | | | | | | | | | | | | | | | | | | | | | |

**COMMERCIAL ENERGY EFFICIENCY**

**2024 INTERNATIONAL ENERGY CONSERVATION CODE®**

**169**

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE C406.2(7)—BASE ENERGY CREDITS FOR GROUP E OCCUPANCIESa** | | | | | | | | | | | | | | | | | | | | | |
| **ID** | **ENERGY CREDIT MEASURE** | **SECTION** | **CLIMATE ZONE** | | | | | | | | | | | | | | | | | | |
| **0A** | **0B** | **1A** | **1B** | **2A** | **2B** | **3A** | **3B** | **3C** | **4A** | **4B** | **4C** | **5A** | **5B** | **5C** | **6A** | **6B** | **7** | **8** |
| E01 | Envelope performance | C406.2.1.1 | Determined in accordance with Section C406.2.1.1 | | | | | | | | | | | | | | | | | | |
| E02 | UA reduction (15%) | C406.2.1.2 | 8 | 18 | 7 | 19 | 12 | 13 | 20 | 17 | 11 | 24 | 20 | 17 | 33 | 32 | 29 | 40 | 38 | 46 | 44 |
| E03 | Reduced air leakage | C406.2.1.3 | 4 | 3 | 3 | 3 | 2 | 5 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1 |
| E04 | Add roof insulation | C406.2.1.4 | 8 | 8 | 4 | 9 | 5 | 7 | 16 | 7 | 1 | 14 | 7 | 10 | 18 | 13 | 13 | 23 | 25 | 22 | 28 |
| E05 | Add wall insulation | C406.2.1.5 | 5 | 7 | 4 | 8 | 3 | 6 | 8 | 6 | 2 | 6 | 3 | 6 | 5 | 5 | 6 | 7 | 6 | 7 | 8 |
| E06 | Improve fenestration | C406.2.1.6 | 8 | 10 | 6 | 9 | 11 | 11 | 15 | 9 | 1 | 16 | 8 | 15 | 22 | 18 | 19 | 33 | 29 | 19 | 18 |
| H01 | HVAC performance | C406.2.2.1 | 30 | 28 | 25 | 26 | 23 | 21 | 20 | 18 | 15 | 19 | 18 | 17 | 19 | 20 | 15 | 23 | 20 | 25 | 29 |
| H02 | Heating efficiency | C406.2.2.2 | x | x | x | x | x | x | 4 | 3 | 3 | 5 | 5 | 10 | 9 | 11 | 6 | 15 | 11 | 18 | 26 |
| H03 | Cooling efficiency | C406.2.2.3 | 9 | 8 | 6 | 7 | 5 | 4 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | x | x | x | x |
| H04 | Residential HVAC control | C406.2.2.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| H05 | DOAS/fan control | C406.2.2.5 | 45 | 42 | 37 | 41 | 36 | 34 | 41 | 39 | 30 | 43 | 46 | 58 | 57 | 65 | 40 | 79 | 63 | 88 | 117 |
| W01 | SHW preheat recovery | C406.2.3.1 a | 7 | 7 | 9 | 8 | 10 | 11 | 13 | 13 | 15 | 14 | 15 | 15 | 15 | 14 | 17 | 13 | 15 | 14 | 12 |
| W02 | Heat pump water heater | C406.2.3.1 b | 4 | 4 | 6 | 5 | 7 | 7 | 9 | 9 | 10 | 10 | 10 | 11 | 11 | 10 | 12 | 10 | 11 | 10 | 9 |
| W03 | Efficient gas water heater | C406.2.3.1 c | 4 | 4 | 6 | 5 | 6 | 7 | 8 | 8 | 9 | 9 | 9 | 10 | 9 | 9 | 11 | 8 | 10 | 9 | 7 |
| W04 | SHW pipe insulation | C406.2.3.2 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 5 | 6 | 5 | 5 | 6 | 5 | 5 | 7 | 4 | 5 | 4 | 4 |
| W05 | Point of use water heaters | C406.2.3.3 a | 3 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 6 | 5 | 5 | 5 | 5 | 5 | 6 | 4 | 5 | 4 | 3 |
| W06 | Thermostatic bal. valves | C406.2.3.3 b | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 2 | 1 | 1 |
| W07 | SHW heat trace system | C406.2.3.3 c | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 6 | 7 | 6 | 6 | 7 | 6 | 6 | 8 | 5 | 7 | 5 | 5 |
| W08 | SHW submeters | C406.2.3.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| W09 | SHW flow reduction | C406.2.3.5 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| W10 | Shower heat recovery | C406.2.3.6 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 4 | 3 | 3 | 4 | 3 | 3 | 4 | 3 | 3 | 3 | 3 |
| P01 | Energy monitoring | C406.2.4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 |
| L01 | Lighting performance | C406.2.5.1 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| L02 | Lighting dimming & tuning | C406.2.5.2 | 5 | 5 | 5 | 6 | 6 | 6 | 5 | 6 | 7 | 6 | 6 | 6 | 5 | 5 | 6 | 4 | 4 | 3 | 2 |
| L03 | Increase occp. sensor | C406.2.5.3 | 4 | 4 | 5 | 5 | 5 | 6 | 6 | 6 | 7 | 6 | 6 | 5 | 4 | 4 | 5 | 3 | 4 | 3 | 2 |
| L04 | Increase daylight area | C406.2.5.4 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 8 | 6 | 6 | 6 | 5 | 5 | 6 | 5 | 5 | 5 | 4 |
| L05 | Residential light control | C406.2.5.5 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| L06 | Light power reduction | C406.2.5.6 | 6 | 7 | 7 | 7 | 8 | 8 | 8 | 8 | 10 | 7 | 8 | 7 | 6 | 7 | 8 | 5 | 6 | 4 | 2 |
| Q01 | Efficient elevator | C406.2.6.1 | 3 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 5 | 4 | 3 |
| Q02 | Commercial kitchen equip. | C406.2.6.2 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| Q03 | Residential kitchen equip. | C406.2.6.3 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| Q04 | Fault detection | C406.2.6.4 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 2 | 3 | 3 | 3 | 3 | 3 | 2 | 4 | 3 | 4 | 4 |
| DOAS = Dedicated Outside Air System; HVAC = Heating, Ventilation and Air Conditioning; SHW = Service Hot Water; UA = *U*-Factor × Area.  a. “x” indicates measure is not available in that climate zone for that measure. | | | | | | | | | | | | | | | | | | | | | |

**COMMERCIAL ENERGY EFFICIENCY**

**170**

**2024 INTERNATIONAL ENERGY CONSERVATION CODE®**

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE C406.2(8)—BASE ENERGY CREDITS FOR GROUP S-1 AND S-2 OCCUPANCIESa** | | | | | | | | | | | | | | | | | | | | | |
| **ID** | **ENERGY CREDIT MEASURE** | **SECTION** | **CLIMATE ZONE** | | | | | | | | | | | | | | | | | | |
| **0A** | **0B** | **1A** | **1B** | **2A** | **2B** | **3A** | **3B** | **3C** | **4A** | **4B** | **4C** | **5A** | **5B** | **5C** | **6A** | **6B** | **7** | **8** |
| E01 | Envelope performance | C406.2.1.1 | Determined in accordance with Section C406.2.1.1 | | | | | | | | | | | | | | | | | | |
| E02 | UA reduction (15%) | C406.2.1.2 | 14 | 14 | 1 | 12 | 1 | 9 | 27 | 16 | 2 | 37 | 29 | 39 | 44 | 47 | 50 | 43 | 52 | 55 | 74 |
| E03 | Reduced air leakage | C406.2.1.3 | 2 | 2 | 1 | 2 | 1 | 3 | 31 | 3 | 1 | 77 | 14 | 17 | 92 | 25 | 8 | 95 | 71 | 69 | 26 |
| E04 | Add roof insulation | C406.2.1.4 | 13 | 12 | 10 | 11 | 10 | 11 | 18 | 17 | 7 | 14 | 19 | 18 | 14 | 20 | 22 | 10 | 14 | 12 | 19 |
| E05 | Add wall insulation | C406.2.1.5 | 19 | 23 | 13 | 21 | 7 | 10 | 15 | 12 | 3 | 10 | 12 | 13 | 9 | 12 | 12 | 7 | 9 | 9 | 8 |
| E06 | Improve fenestration | C406.2.1.6 | 7 | 5 | 8 | 7 | 6 | 6 | 2 | 4 | 2 | 4 | 1 | 6 | 5 | 1 | 7 | 3 | 4 | 4 | 7 |
| H01 | HVAC performance | C406.2.2.1 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| H02 | Heating efficiency | C406.2.2.2 | x | x | x | x | x | x | 16 | 3 | 1 | 33 | 17 | 22 | 41 | 31 | 21 | 44 | 38 | 43 | 43 |
| H03 | Cooling efficiency | C406.2.2.3 | 7 | 7 | 4 | 5 | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | x | x | x | x |
| H04 | Residential HVAC control | C406.2.2.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| H05 | DOAS/fan control | C406.2.2.5 | 35 | 37 | 26 | 33 | 24 | 27 | 77 | 35 | 14 | 141 | 83 | 96 | 168 | 132 | 90 | 180 | 157 | 177 | 178 |
| W01 | SHW preheat recovery | C406.2.3.1 a | 8 | 7 | 9 | 8 | 10 | 10 | 8 | 10 | 12 | 5 | 8 | 8 | 4 | 6 | 9 | 3 | 4 | 3 | 3 |
| W02 | Heat pump water heater | C406.2.3.1 b | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 1 | 2 | 2 | 1 | 2 | 2 | 1 | 1 | 1 | 1 |
| W03 | Efficient gas water heater | C406.2.3.1 c | 4 | 4 | 5 | 4 | 5 | 5 | 4 | 5 | 6 | 3 | 4 | 4 | 2 | 3 | 5 | 2 | 2 | 2 | 2 |
| W04 | SHW pipe insulation | C406.2.3.2 | 3 | 3 | 4 | 3 | 3 | 3 | 2 | 3 | 4 | 2 | 2 | 3 | 1 | 2 | 3 | 1 | 1 | 1 | 1 |
| W05 | Point of use water heaters | C406.2.3.3 a | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| W06 | Thermostatic bal. valves | C406.2.3.3 b | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |
| W07 | SHW heat trace system | C406.2.3.3 c | 4 | 4 | 4 | 3 | 4 | 4 | 3 | 4 | 5 | 2 | 3 | 3 | 2 | 2 | 4 | 2 | 2 | 2 | 2 |
| W08 | SHW submeters | C406.2.3.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| W09 | SHW flow reduction | C406.2.3.5 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| W10 | Shower heat recovery | C406.2.3.6 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| P01 | Energy monitoring | C406.2.4 | 5 | 5 | 6 | 6 | 6 | 6 | 5 | 6 | 6 | 5 | 5 | 5 | 5 | 5 | 6 | 5 | 5 | 5 | 5 |
| L01 | Lighting performance | C406.2.5.1 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| L02 | Lighting dimming & tuning | C406.2.5.2 | 10 | 10 | 12 | 11 | 12 | 14 | 9 | 12 | 14 | 6 | 9 | 9 | 3 | 6 | 9 | 3 | 5 | 3 | 2 |
| L03 | Increase occp. sensor | C406.2.5.3 | 12 | 12 | 14 | 13 | 15 | 14 | 12 | 14 | 17 | 7 | 11 | 11 | 5 | 7 | 11 | 4 | 6 | 3 | 3 |
| L04 | Increase daylight area | C406.2.5.4 | 15 | 14 | 18 | 16 | 18 | 17 | 13 | 16 | 21 | 7 | 12 | 11 | 5 | 8 | 10 | 4 | 6 | 6 | 5 |
| L05 | Residential light control | C406.2.5.5 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| L06 | Light power reduction | C406.2.5.6 | 14 | 14 | 17 | 16 | 17 | 17 | 13 | 17 | 19 | 8 | 13 | 12 | 5 | 8 | 12 | 4 | 6 | 4 | 2 |
| Q01 | Efficient elevator | C406.2.6.1 | 15 | 14 | 18 | 16 | 18 | 18 | 15 | 18 | 21 | 9 | 14 | 14 | 7 | 10 | 14 | 5 | 7 | 5 | 5 |
| Q02 | Commercial kitchen equip. | C406.2.6.2 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| Q03 | Residential kitchen equip. | C406.2.6.3 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| Q04 | Fault detection | C406.2.6.4 | 3 | 3 | 2 | 3 | 2 | 2 | 3 | 2 | 1 | 5 | 3 | 3 | 5 | 4 | 3 | 6 | 5 | 6 | 6 |
| DOAS = Dedicated Outside Air System; HVAC = Heating, Ventilation and Air Conditioning; SHW = Service Hot Water; UA = *U*-Factor × Area.  a. “x” indicates creditis not available in that climate zone for that measure. | | | | | | | | | | | | | | | | | | | | | |

**COMMERCIAL ENERGY EFFICIENCY**

**2024 INTERNATIONAL ENERGY CONSERVATION CODE®**

**171**

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE C406.2(9)—BASE ENERGY CREDITS FOR OTHER OCCUPANCIESa, b** | | | | | | | | | | | | | | | | | | | | | |
| **ID** | **ENERGY CREDIT MEASURE** | **SECTION** | **CLIMATE ZONE** | | | | | | | | | | | | | | | | | | |
| **0A** | **0B** | **1A** | **1B** | **2A** | **2B** | **3A** | **3B** | **3C** | **4A** | **4B** | **4C** | **5A** | **5B** | **5C** | **6A** | **6B** | **7** | **8** |
| E01 | Envelope performance | C406.2.1.1 | Determined in accordance with Section C406.2.1.1 | | | | | | | | | | | | | | | | | | |
| E02 | UA reduction (15%) | C406.2.1.2 | 7 | 8 | 3 | 7 | 5 | 5 | 11 | 7 | 2 | 18 | 10 | 14 | 26 | 20 | 19 | 24 | 25 | 29 | 32 |
| E03 | Reduced air leakage | C406.2.1.3 | 6 | 4 | 5 | 4 | 3 | 7 | 12 | 3 | 2 | 28 | 5 | 6 | 36 | 9 | 3 | 41 | 27 | 33 | 15 |
| E04 | Add roof insulation | C406.2.1.4 | 4 | 4 | 3 | 4 | 4 | 4 | 8 | 6 | 2 | 7 | 6 | 7 | 9 | 8 | 9 | 9 | 10 | 9 | 12 |
| E05 | Add wall insulation | C406.2.1.5 | 16 | 19 | 11 | 17 | 5 | 6 | 10 | 7 | 2 | 9 | 6 | 8 | 9 | 7 | 7 | 9 | 9 | 10 | 8 |
| E06 | Improve fenestration | C406.2.1.6 | 4 | 4 | 3 | 4 | 5 | 6 | 6 | 4 | 1 | 9 | 4 | 7 | 11 | 7 | 6 | 16 | 14 | 8 | 8 |
| H01 | HVAC performance | C406.2.2.1 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| H02 | Heating efficiency | C406.2.2.2 | x | x | x | x | x | x | 6 | 2 | 3 | 11 | 6 | 8 | 15 | 11 | 9 | 18 | 15 | 19 | 23 |
| H03 | Cooling efficiency | C406.2.2.3 | 7 | 7 | 5 | 5 | 4 | 3 | 1 | 2 | 1 | x | x | x | x | x | x | x | x | x | x |
| H04 | Residential HVAC control | C406.2.2.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| H05 | DOAS/fan control | C406.2.2.5 | 37 | 36 | 31 | 34 | 30 | 28 | 43 | 32 | 23 | 61 | 42 | 49 | 75 | 61 | 49 | 90 | 77 | 93 | 90 |
| W01 | SHW preheat recovery | C406.2.3.1 a | 18 | 19 | 22 | 21 | 25 | 26 | 28 | 29 | 34 | 29 | 31 | 34 | 29 | 31 | 35 | 26 | 29 | 27 | 26 |
| W02 | Heat pump water heater | C406.2.3.1 b | 12 | 12 | 15 | 14 | 17 | 17 | 20 | 20 | 24 | 21 | 22 | 25 | 21 | 23 | 26 | 20 | 22 | 21 | 20 |
| W03 | Efficient gas water heater | C406.2.3.1 c | 11 | 11 | 13 | 13 | 15 | 16 | 17 | 17 | 21 | 18 | 19 | 21 | 18 | 19 | 22 | 16 | 18 | 17 | 16 |
| W04 | SHW pipe insulation | C406.2.3.2 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 4 | 4 | 5 | 4 | 4 | 5 | 3 | 4 | 3 | 3 |
| W05 | Point of use water heaters | C406.2.3.3 a | 8 | 10 | 11 | 10 | 11 | 12 | 12 | 12 | 14 | 13 | 13 | 14 | 13 | 13 | 14 | 11 | 12 | 12 | 11 |
| W06 | Thermostatic bal. valves | C406.2.3.3 b | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 1 |
| W07 | SHW heat trace system | C406.2.3.3 c | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 7 | 6 | 6 | 7 | 5 | 6 | 7 | 5 | 5 | 5 | 5 |
| W08 | SHW submeters | C406.2.3.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| W09 | SHW flow reduction | C406.2.3.5 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| W10 | Shower heat recovery | C406.2.3.6 | 6 | 6 | 7 | 7 | 8 | 9 | 10 | 10 | 11 | 10 | 11 | 12 | 10 | 11 | 12 | 10 | 11 | 10 | 10 |
| P01 | Energy monitoring | C406.2.4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 |
| L01 | Lighting performance | C406.2.5.1 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| L02 | Lighting dimming & tuning | C406.2.5.2 | 5 | 5 | 5 | 5 | 6 | 6 | 5 | 6 | 7 | 5 | 5 | 5 | 4 | 4 | 5 | 3 | 4 | 3 | 2 |
| L03 | Increase occp. sensor | C406.2.5.3 | 5 | 6 | 6 | 6 | 7 | 7 | 6 | 7 | 8 | 5 | 6 | 6 | 4 | 5 | 6 | 3 | 4 | 3 | 2 |
| L04 | Increase daylight area | C406.2.5.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| L05 | Residential light control | C406.2.5.5 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| L06 | Light power reduction | C406.2.5.6 | 7 | 7 | 8 | 7 | 8 | 8 | 7 | 8 | 9 | 5 | 7 | 6 | 4 | 5 | 6 | 4 | 4 | 3 | 2 |
| Q01 | Efficient elevator | C406.2.6.1 | 4 | 4 | 5 | 4 | 5 | 5 | 5 | 5 | 6 | 4 | 5 | 5 | 4 | 4 | 5 | 3 | 4 | 3 | 3 |
| Q02 | Commercial kitchen equip. | C406.2.6.2 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| Q03 | Residential kitchen equip. | C406.2.6.3 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| Q04 | Fault detection | C406.2.6.4 | 3 | 3 | 3 | 3 | 3 | 2 | 3 | 2 | 2 | 3 | 3 | 2 | 3 | 3 | 2 | 4 | 3 | 4 | 4 |
| DOAS = Dedicated Outside Air System; HVAC = Heating, Ventilation and Air Conditioning; SHW = Service Hot Water; UA = *U*-Factor × Area.   1. “x” indicates credit is not available in that climate zone for that measure. 2. Other occupancy groups include all groups except Groups A-2, B, E, I, M, S and R. | | | | | | | | | | | | | | | | | | | | | |

**C406.2.1 More efficient building thermal envelope.** A project shall achieve credits for improved envelope performance by complying with one of the following measures:

1. Section C406.2.1.1: E01.
2. Section C406.2.1.2: E02.
3. Section C406.2.1.3: E03.
4. Both E02 and E03.
5. Any combination of:
   1. Section C406.2.1.3: E03.
   2. Section C406.2.1.4: E04.
   3. Section C406.2.1.5: E05.
   4. Section C406.2.1.6: E06.

**C406.2.1.1 E01 Improved envelope performance ASHRAE 90.1 Appendix C.** *Building thermal envelope* measures shall be installed to improve the energy performance of the project. The achieved energy credits shall be determined using Equation 4-13.

**Equation 4-13** *ECENV* = 1,000 × (*EPFB* - *EPFP*)/*EPFB*

where:

*ECENV* = E01 measure energy credits.

*EPFB* = base envelope performance factor calculated in accordance with ASHRAE 90.1 Appendix C.

*EPFP* = proposed envelope performance factor calculated in accordance with ASHRAE 90.1 Appendix C.

**C406.2.1.2 E02 Component performance envelope reduction.** Energy credits shall be achieved where the component performance of the *building thermal envelope* as designed is not less than 15 percent below the component performance of the *building thermal envelope* in accordance with Section C402.1.4.

**C406.2.1.3 E03 Reduced air leakage.** Energy credits shall be achieved where tested building *air leakage* is not less than 10 percent of the maximum leakage permitted by Section C402.6.2, provided that the *building* is tested in accordance with the applicable method in Section C402.6.2. Energy credits achieved for measure E03 shall be determined as follows:

**Equation 4-14** *EC*E03 = *ECB* × *ECadj*

where:

*EC*E03 = Energy efficiency credits achieved for envelope leakage reduction. *ECB* = Section C406.2.1.3 credits from Tables C406.2(1) through C406.2(9). *ECadj* = *Ls* /*ECa*

*Ls* = Leakage savings fraction: the lesser of [(*Lr*– *Lm* )/*Lr* ] or 0.8.

*Lr* = Maximum leakage permitted for tested buildings, by occupancy group, in accordance with Section C402.6.2.

*Lm* = Measured leakage in accordance with Section C402.6.2.1 or C402.6.2.2.

*ECa* = Energy credit alignment factor: 0.37 for whole-building tests in accordance with Section C402.6.2.1 or 0.25 for dwelling and sleeping unit enclosure tests in accordance with Section C402.6.2.2.

**C406.2.1.4 E04 Added roof insulation.** Energy credits shall be achieved for insulation that is in addition to the required insu- lation in Table C402.1.3. All roof areas in the project shall have additional R-10 *continuous insulation* included in the *roof assembly*. For attics, this is permitted to be achieved with fill or batt insulation rated at R-10 that is continuous and not inter- rupted by ceiling or roof joists. Where interrupted by joists, the added insulation shall be not less than R-13. Alternatively, one- half of the base credits shall be achieved where the added *R-value* is one-half of the additional *R-value* required by this section.

**C406.2.1.5 E05 Added wall insulation.** Energy credits shall be achieved for insulation applied to not less than 90 percent of all opaque wall area in the project that is in addition to the required insulation in Table C402.1.3. Opaque walls shall have addi- tional R-5 *continuous insulation* included in the wall assembly. Alternatively, one-half of the base credits shall be achieved where the added *R-value* is R-2.5.

**C406.2.1.6 E06 Improve fenestration.** Energy credits shall be achieved for improved energy characteristics of all vertical *fenestration* in the project meeting the requirements in Table C406.2.1.6. The area-weighted average *U-factor* and SHGC of all vertical *fenestration* shall be equal to or less than the value shown in the table. Where vertical *fenestration* is located under a permanently attached shading projection with a projection factor (PF) not less than 0.2 as determined in accordance with Section C402.5.3, the SHGC for that *fenestration* shall be permitted to be divided by 1.2. The area-weighted average *visible transmittance* (VT) of all vertical *fenestration* shall be equal to or greater than the value shown in the table.

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **TABLE C406.2.1.6—VERTICAL FENESTRATION REQUIREMENTS FOR ENERGY CREDIT E06** | | | | |
| **APPLICABLE CLIMATE ZONE** | **MAXIMUM *U*-FACTOR** | | **MAXIMUM SHGC** | **MINIMUM VT** |
| **Fixed** | **Operable** |
| 0–2 | 0.45 | 0.52 | 0.21 | 0.28 |
| 3 | 0.33 | 0.44 | 0.23 | 0.30 |
| 4–5 | 0.31 | 0.38 | 0.34 | 0.41 |
| 6–7 | 0.26 | 0.32 | 0.38 | 0.44 |
| 8 | 0.24 | 0.28 | 0.38 | 0.44 |

**C406.2.2 More efficient HVAC equipment performance.** All heating and cooling systems shall meet the minimum requirements of Section C403 and efficiency improvements shall be referenced to minimum efficiencies listed in tables referenced by Section C403.3.2. Where multiple efficiency requirements are listed, equipment shall meet the seasonal or part-load efficiencies including SEER, integrated energy efficiency ratio (IEER), *integrated part load value* (IPLV) or AFUE. Equipment that is larger than the maxi- mum capacity range indicated in tables referenced by Section C403.3.2 shall utilize the values listed for the largest capacity equipment for the associated equipment type shown in the table. Where multiple individual heating or cooling systems serve the project, the improvement shall be the weighted-average improvement based on individual system capacity. Systems are permit- ted to achieve HVAC energy credits by meeting the requirements of one of the following:

1. C406.2.2.1 H01.
2. C406.2.2.2 H02.
3. C406.2.2.3 H03.
4. C406.2.2.4 H04.
5. C406.2.2.5 H05.
6. Any combination of H02, H03, H04 and H05.
7. The combination of H01 and H04.

**C406.2.2.1 H01 HVAC Total System Performance Ratio (TSPR).** H01 energy credits shall be earned where systems are permitted to use Section C409 and where the savings (*TSPRs*) based on the proposed TSPR (*TSPRp*) compared to the target TSPR is 5 percent or more. If savings are greater than 5 percent, determine H01 earned credits using Equation 4-15. Energy credits for H01 shall not be combined with energy credits from HVAC measures H02, H03 or H05.

**Equation 4-15** *ECTSPR* = *ECBASE* × *AREATSPR* × *TSPRS*/0.05

*ECTSPR* = Energy credits achieved for H01.

*ECBASE* = H01 base energy credits from Tables C406.2(1) through C406.2(9).

*TSPRs* = The lesser of 0.20 and [1 – (*TSPRt* /*TSPRp* )]. where:

*AREATSPR* = (floor area served by systems included in TSPR)/(total building conditioned floor area)

*TSPRp* = HVAC TSPR of the proposed design calculated in accordance with Sections C409.4, C409.5 and C409.6.

*TSPRt* = *TSPRr* /*MPF*.

*TSPRr* = HVAC TSPR of the reference building design calculated in accordance with Sections C409.4, C409.5 and C409.6. *MPF* = Mechanical performance factor from Table C409.4 based on climate zone and building use type. Where a build- ing has multiple building use types, *MPF* shall be area weighted in accordance with Section C409.4.

**C406.2.2.2 H02 More efficient HVAC equipment heating performance.** In accordance with Section C406.1.1, not less than 90 percent of the total HVAC heating capacity serving the total *conditioned floor area* of the entire *building* or tenant space shall comply with the requirements of this section.

* 1. Equipment installed shall be types that have their efficiency listed in tables referenced by Section C403.3.2. Electric resistance heating capacity shall be limited to 20 percent of system capacity, with the exception of heat pump supple- mental heating.
  2. Equipment shall exceed the minimum heating efficiency requirements listed in tables referenced by Section C403.3.2 by not less than 5 percent. Where equipment exceeds the minimum annual heating efficiency requirements by more

than 5 percent, energy efficiency credits for heating shall be determined using Equation 4-16, rounded to the nearest whole number.

**Equation 4-16** *EECHEH* = *EEC*H5 × (*HEI*/0.05)

where:

*EECHEH* = Energy efficiency credits for heating efficiency improvement.

*EEC*H5 = Section C406.2.2.2 credits from Tables C406.2(1) through C406.2(9).

*HEI* = The lesser of the improvement above minimum heating efficiency requirements, expressed as a fraction, or 20 percent (0.20). Where heating equipment with different minimum efficiencies are included in the building, a heating capacity weighted-average improvement shall be used. Where electric resistance primary heating or reheat is included in the building, it shall be included in the weighted-average improvement with an HEI of 0. Supplemental gas and elec- tric heat for heat pump systems shall be excluded from the weighted HEI. For heat pumps rated at multiple ambient temperatures, the efficiency at 47°F (8.3°C) shall be used. For metrics that increase as efficiency increases, HEI shall be calculated as follows:

*HEI* = (*HMDES* /*HMMIN* ) – 1

where:

*HMDES* = Design heating efficiency metric, part-load or annualized where available.

*HMMIN* = Minimum required heating efficiency metric, part-load or annualized where available from Section C403.3.2.

**Exception:** In low-energy spaces complying with Section C402.1.1, not less than 90 percent of the installed heating capacity is provided by electric infrared or gas-fired radiant heating equipment for localized heating applications. Such spaces shall achieve base energy credits only for *EEC*H5.

**C406.2.2.3 H03 More efficient HVAC cooling equipment and fan performance.** In accordance with Section C406.1.1, not less than 90 percent of the total HVAC cooling capacity serving the total *conditioned floor area* of the entire *building* or tenant space shall comply with all of the requirements of this section.

1. Equipment installed shall be types that are listed in tables referenced by Section C403.3.2.
2. Equipment shall exceed the minimum cooling efficiency requirements listed in tables referenced by Section C403.3.2 by not less than 5 percent. For water-cooled chiller plants, heat-rejection equipment performance in Table C403.3.2(7) shall also be increased by at least the chiller efficiency improvement. Where equipment exceeds both the minimum annual cooling efficiency and heat-rejection efficiency requirements by more than 5 percent, energy effi- ciency credits for cooling shall be determined using Equation 4-17, rounded to the nearest whole number.

Where fan energy is not included in the packaged equipment rating or it is and the fan size has been increased from the as- rated equipment condition, fan power or horsepower shall be less than 95 percent of the allowed fan power in Section C403.8.1.

**Equation 4-17** *EECHEH* = *EEC*H5 × (*CEI*/0.05)

*EECHEC* = Energy efficiency credits for cooling efficiency improvement.

*EEC*5 = Section C406.2.2.3 base energy credits from Tables C406.2(1) through C406.2(9).

*CEI* = The lesser of the improvement above minimum cooling efficiency and heat-rejection performance requirements, expressed as a fraction, or 20 percent (0.20). Where cooling equipment with different minimum efficiencies is included in the building, a cooling capacity weighted-average improvement shall be used. Where multiple cooling efficiency or performance requirements are provided, the equipment shall exceed the annualized energy or part-load requirement. Meeting both part-load and full-load efficiencies is not required.

For metrics that increase as efficiency increases, *CEI* shall be calculated as follows:

*CEI* = (*CMDES* /*CMMIN* ) – 1. For metrics that decrease as efficiency increases, *CEI* shall be calculated as follows:

*CEI* = (*CMMIN* /*CMDES* ) – 1.

where:

*CMDES* = Design cooling efficiency metric, part-load or annualized where available.

*CMMIN* = Minimum required cooling efficiency metric, part-load or annualized where available from Section C403.3.2.

For data centers using ASHRAE Standard 90.4, *CEI* shall be calculated as follows:

*CEI* = (*AMLCMAX* /*AMLCDES* ) – 1

where:

*AMLCDES* = As-designed annualized mechanical load component calculated in accordance with ASHRAE Standard 90.4, Section 6.5.

*AMLCMAX* = Maximum annualized mechanical load component from ASHRAE Standard 90.4, Table 6.5.

**C406.2.2.4 H04 Residential HVAC control.** HVAC systems serving *dwelling units* or *sleeping units* shall be controlled to auto- matically activate a setback at least 5°F (3°C) for both heating and cooling. The temperature controller shall be configured to

provide setback during occupied sleep periods. The unoccupied setback mode shall be configured to operate in conjunction with one of the following:

1. A *manual* main control device by each *dwelling unit* main entrance that initiates setback and nonventilation mode for all HVAC units in the *dwelling unit* and is clearly identified as “Heating/Cooling Master Setback.”
2. Occupancy sensors in each room of the *dwelling unit* combined with a door switch to initiate setback and nonventila- tion mode for all HVAC units in the dwelling within 20 minutes of all spaces being vacant immediately after a door switch operation. Where separate room HVAC units are used, an individual occupancy sensor on each unit that is configured to provide setback shall meet this requirement.
3. An advanced learning *thermostat* or controller that recognizes occupant presence and automatically creates a sched- ule for occupancy and provides a dynamic setback schedule based on when the spaces are generally unoccupied.
4. An automated control and sensing system that uses geographic fencing connected to the *dwelling unit* occupants’ cell phones and initiates the setback condition when all occupants are away from the *building*.

**C406.2.2.5 H05 Dedicated outdoor air system.** Credits for this measure are allowed only where single-*zone* HVAC units are not required to have multispeed or variable-speed fan control in accordance with Section C403.8.6.1. HVAC controls and venti- lation systems shall include all of the following:

1. *Zone* controls shall cycle the heating/cooling unit fans off when not providing required heating and cooling or shall limit fan power to 0.12 watts/cfm (0.056 w/l/s) of *zone* supply air.
2. Outdoor air shall be supplied by an independent ventilation system designed to provide not more than 130 percent of the minimum outdoor air to each individual occupied *zone*, as specified by the *International Mechanical Code*.

**Exception:** Outdoor airflow is permitted to increase during emergency or economizer operation, implemented as described in Item 4.

1. The ventilation system shall have energy recovery with an *enthalpy recovery ratio* of 65 percent or more at heating design conditions in Climate Zones 3 through 8 and an *enthalpy recovery ratio* of 65 percent or more at cooling design conditions in Climate Zones 0, 1, 2, 3A, 3B, 4A, 4B, 5A and 6A. In “A” *climate zones*, energy recovery shall include latent recovery. Where no humidification is provided, heating energy recovery effectiveness is permitted to be based on *sensible energy recovery ratio*. Where energy recovery effectiveness is less than the 65 percent required for full credit, adjust the credits from Section C406.2 by the factors in Table C406.2.2.5.
2. Where the ventilation system serves multiple *zones* and the system is not in a latent recovery outside air dehumidifi- cation mode, partial economizer cooling through an outdoor air bypass or wheel speed control shall automatically do one of the following:
   1. Set the energy recovery leaving-air temperature 55°F (13°C) or 100 percent outdoor air bypass when a major- ity of *zones* require cooling and outdoor air temperature is below 70°F (21°C).
   2. The HVAC ventilation system shall include supply-air temperature controls that automatically reset the supply-air temperature in response to representative *building* loads, or to outdoor air temperatures. The controls shall reset the supply-air temperature not less than 25 percent of the difference between the design supply-air temperature and the design room-air temperature.
3. Ventilation systems providing mechanical dehumidification shall use recovered energy for reheat within the limits of Item 4. This shall not limit the use of latent energy recovery for dehumidification.

Where only a portion of the *building* is permitted to be served by constant air volume units or the *enthalpy recovery ratio* or *sensible energy recovery ratio* is less than 65 percent, the base energy credits shown in Section C406.2 shall be prorated as follows:

**Equation 4-18** *ECDOAS* = *ECBASE* × *FLOORCAV* × *EREADJ*

where:

*ECDOAS* = Energy credits achieved for H05.

*ECBASE* = H05 base energy credits in Section C406.2.

*FLOORCAV* = Fraction of whole-project gross conditioned floor area not required to have variable-speed or multi-speed fan airflow control in accordance with Section C403.8.6.

*EREadj* = The energy recovery adjustment from Table C406.2.2.5 based on the lower of actual cooling or heating enthalpy recovery ratio or sensible energy recovery ratio where required for the climate zone. Where recovery ratios vary, use a weighted average by supply airflow.

|  |  |  |
| --- | --- | --- |
| **TABLE C406.2.2.5—DOAS ENERGY RECOVERY ADJUSTMENTS** | | |
| ***EREadj* BASED ON LOWER OF ACTUAL HEATING OR COOLING ENERGY RECOVERY EFFECTIVENESS WHERE REQUIRED** | | |
| **Cooling *Err* Is at Least** | **Heating Enthalpy Recovery Ratio**  **or Sensible Energy Recovery Ratio Is at Least** | **Energy Recovery Effectiveness Adjustment (*EREadj*)** |
| 65% | 65% | 1.00 |
| 60% | 60% | 0.67 |
| 55% | 55%a | 0.33 |
| 50% | 50%a | 0.25 |
| a. In climate zones where heating recovery is required in Section C403, a heating recovery effectiveness below 60 percent is not allowed for dwelling units. | | |

**C406.2.3 Reduced energy use in service water heating.** For projects with service water heating equipment that serves the whole *building*, a *building addition* or a tenant space shall achieve credits through compliance with the requirements of this section. Systems are permitted to achieve energy credits by meeting the requirements of one of the following:

1. Section C406.2.3.1 by selecting one allowed measure W01, W02, W03 or a combination in accordance with Section C406.2.3.1.4.
2. Section C406.2.3.2 W04.
3. Section C406.2.3.3 by selecting one allowed measure: W05, W06 or W07.
4. Section C406.2.3.4 W08.
5. Section C406.2.3.5 W09.
6. Section C406.2.3.6 W10.
7. Any combination of measures in Sections C406.2.3.1 through C406.2.3.6 as long as not more than one allowed measure from Sections C406.2.3.1 and C406.2.3.3 are selected.

**C406.2.3.1 Service water heating system efficiency.** A project is allowed to achieve energy credits from only one of Sections C406.2.3.1.1 through C406.2.3.1.4.

**C406.2.3.1.1 W01 Recovered or renewable water heating.** The *building* service water-heating system shall have one or more of the following that are sized to provide not less than 30 percent of the *building’s* annual hot water requirements, or sized to provide not less than 70 percent of the *building’s* annual hot water requirements if the *building* is required to comply with Section C403.11.5:

* 1. Waste heat recovery from service hot water, heat recovery chillers, *building* equipment or process equipment.
  2. A water-to-water heat pump that precools chilled water return for *building* cooling while heating SHW.
  3. On-site renewable energy water-heating systems.

**C406.2.3.1.2 W02 Heat pump water heater.** Air-source heat pump *water heaters* shall be installed according to the manu- facturer’s instructions and at least 30 percent of design end-use *service water heating* requirements shall be met using only heat pump heating at an ambient condition of 67.5°F (19.7°C), db without supplemental electric resistance or fossil fuel heat- ing. For a heat pump *water heater* with supplemental electric resistance heating, the heat pump-only capacity shall be deemed at 40 percent of first-hour draw. Where the heat pump-only capacity exceeds 50 percent of the design end-use load, excluding recirculating system losses, the credits from the Section C406.2 tables shall be prorated as follows:

**Equation 4-19** *ECHPWH* = (*ECBASE*/0.5) × {(*CAPHPWH*)/(Endload)[not greater than 2]} where:

*ECHPWH* = Energy credits achieved for W02.

*ECBASE* = W02 base energy credits from Tables C406.2(1) through C406.2(9).

Endload = End-use peak hot water load, excluding load for heat trace or recirculation, Btu/h or kW.

*CAPHPWH* = The heat pump-only capacity at 50°F (10°C) entering air and 70°F (21°C) entering potable water without supplemental electric resistance or fossil fuel heat, Btu/h or kW.

The heat pump service water heating system shall comply with the following requirements:

1. For systems with an installed total output capacity of more than 100,000 Btu/h (29 kW) at an ambient condition of

67.5°F (19.7°C) db, a preheat storage tank with greater than or equal to 0.75 gallons per 1,000 Btu/h (≥ 9.7 L/kW) of design end-use service water-heating requirements shall be heated only with a heat pump heating when the ambi- ent temperature is greater than 45°F (7.2°C).

1. For systems with piping temperature maintenance, either a heat trace system or a separate water heater in series for recirculating system and final heating shall be installed.
2. Heat pump water heater efficiency shall meet or exceed one of the following:
   1. Output-capacity-weighted-average UEF of 3.0 in accordance with 10 CFR 430 Appendix E.
   2. Output-capacity-weighted-average COP of not less than 4.0 tested at 50°F (10°C) entering air and 70°F (21°C) entering potable water in accordance with ANSI/AHRI 1300.

Where the heat pump capacity at 50°F (10°C) entering air and 70°F (21°C) entering water exceeds 50 percent of the design end-use load, excluding recirculating system losses, the base credits from Section C406.2 shall be prorated based on Equation 4-20.

**Equation 4-20** W02 credit = base W02 table credit × (*HPlf*/50%) where:

*HPlf* = Heat pump capacity as a fraction of the design end-use SHW requirements, excluding recirculating system losses, not to exceed 80 percent.

**C406.2.3.1.3 W03 Efficient fossil fuel water heater.** The combined input-capacity-weighted-average equipment rating of all gas water heating equipment in the *building* shall be not less than 95 percent *Et* or 0.93 UEF. Adjustments shall apply as follows:

1. Where the *service water heating* system is required to comply with Section C404.2.1, this measure shall achieve 30 percent of the listed base W03 energy credits in Tables C406.2(1) through C406.2(9).
2. Where the installed *building service water heating* capacity is less than 200,000 Btu/h (59 kW) and weighted UEF is less than 0.93 UEF and not less than 0.82, this measure shall achieve 25 percent of the base W03 credit in Tables C406.2(1) through C406.2(9).

**C406.2.3.1.4 Combination service water heating systems.** Combination *service water heating* systems shall achieve cred- its using one of the measure combinations as follows:

1. (W01 + W02) Where *service water heating* employs both energy recovery and heat pump water heating, W01 may be combined with W02 and receive the sum of both credits.
2. (W01 + W03) Where *service water heating* employs both energy recovery and efficient gas water heating, W01 may be combined with W03 and receive the sum of the W01 credit and the portion of the W03 credit based on Item 4.
3. (W02 + W03) Where *service water heating* employs both heat pump water heating and efficient gas water heating, W02 may be combined with W03 and receive the sum of the W02 credit and the portion of the W03 credit based on Item 4.
4. For Items 2 and 3, the achieved W03 credit shall be the Section C406.2.3.1.3 W03 credit multiplied by the fractional share of total water-heating installed capacity served by gas water heating that is not less than 95 percent *Et* or

0.93 UEF. In no case shall the achieved W03 credit exceed 60 percent of the W03 credit in the Section C406.2 tables.

In *buildings* that have a service water heating design generating capacity greater than 900,000 Btu/h (264 kW), that proportioned W03 credit shall be further multiplied by 30 percent.

**C406.2.3.2 W04 Service hot water piping insulation increase.** Where service hot water is provided by a central water heating system, the hot water pipe insulation thickness shall be at least 1.5 times the thickness required in Section C404.4. All service hot water piping shall be insulated from the hot water source to the fixture shutoff. Where 50 percent or more of hot water piping does not have increased insulation due to installation in partitions, the credit shall be prorated as a percentage of lineal feet of piping with increased insulation.

**C406.2.3.3 Service water-heating distribution temperature maintenance.** A project is allowed to claim energy credits from only one of the following SHW distribution temperature maintenance measures.

1. **W05 Point of use *water heaters*.** Credits are available for Group B or E *buildings* larger than 5,000 square feet (465 m2) where *service water heating* systems meet the following requirements:
   1. Fixtures requiring hot water shall be supplied from a local *water heater* with no recirculating system or heat trace piping.

**Exception:** Commercial kitchens or showers in locker rooms shall be permitted to have a local recirculating system or heat trace piping where water heaters are located not more than 50 lineal feet (15 m) from the farthest fixture served.

* 1. Supply piping from the *water heater* to the termination of the fixture supply pipe shall be insulated to the levels shown in Table C404.4.1.

Exceptions:

1. Piping at locations where a vertical support of the piping is installed.
2. Where piping passes through a framing member and insulation requires increasing the size of the framing member.
   1. The water volume in the piping from the *water heater* to the termination of any individual fixture shall be limited as follows:
      1. Nonresidential public lavatory faucets that are available for use by members of the general public: not more than 2 ounces (59 mL).
      2. Commercial kitchens or showers in locker rooms with recirculating systems or heat trace piping: not more than 24 ounces (710 mL) from the recirculating system or heat trace piping.
      3. All other plumbing fixtures or appliances: not more than 16 ounces (473 mL).
3. **W06 Thermostatic balancing valves.** Credits are available where *service water heating* is provided centrally and distributed throughout the *building* with a recirculating system. Each recirculating system branch return connection to the main SHW supply piping shall have an *automatic* thermostatic balancing valve set to a minimal return water flow when the branch return temperature is greater than 120°F (49°C).
4. **W07 Heat trace system.** Credits are available for projects with gross floor area greater than 10,000 square feet (929 m2) and a central water heating system. The energy credits achieved shall be from Tables C406.2(1) through C406.2(9). This system shall include self-regulating electric heat cables, connection kits and electronic controls. The cable shall be installed directly on the hot water supply pipes underneath the insulation to replace standby losses.

**C406.2.3.4 W08 Water-heating system submeters.** Each individual *dwelling unit* in a Group R-2 occupancy served by a central service water heating system shall be provided with a service hot water meter connected to a reporting system that provides individual *dwelling unit* reporting of actual domestic hot water use. Preheated water serving the cold water inlet to showers need not be metered.

**C406.2.3.5 W09 Service hot water flow reduction.** *Dwelling unit*, *sleeping unit* and guestroom plumbing fixtures that are connected to the service water-heating system shall have a flow or consumption rating less than or equal to the values shown in Table C406.2.3.5.

|  |  |
| --- | --- |
| **TABLE C406.2.3.5—MAXIMUM FLOW RATING FOR RESIDENTIAL PLUMBING FIXTURES WITH HEATED WATER** | |
| **PLUMBING FIXTURE** | **MAXIMUM FLOW RATE** |
| Faucet for private lavatory,a hand sinks, or bar sinks | 1.2 gpm at 60 psi |
| Faucet for residential kitchen sinka, b, c | 1.8 gpm at 60 psi |
| Shower head (including hand-held shower spray)a, b, d | 1.8 gpm at 80 psi |
| For SI: 1 gallon per minute = 3.785 L/min, 1 pound per square inch = 6.89 kPa.   1. Showerheads, lavatory faucets and kitchen faucets are subject to US federal requirements listed in 10 CFR 430.32(o)–(p). 2. Maximum flow allowed is less than required by flow rates listed in 10 CFR 430.32(o)–(p) for showerheads and kitchen faucets. 3. Residential kitchen faucets may temporarily increase the flow above the maximum rate, but not above 2.2 gallons per minute at 60 psi (8.3 L/min at 414 kPa), and must default to the maximum flow rate listed. 4. Where a shower is served by multiple shower heads, the combined flow rate of all shower heads controlled by a single valve shall not exceed the maximum flow rate listed or the shower shall be designed to allow only one shower head to operate at a time. | |

**C406.2.3.6 W10 Shower drain heat recovery.** Cold water serving *building* showers shall be preheated by shower drain heat recovery units that comply with Section C404.7. The efficiency of drain heat recovery units shall be 54 percent or greater measured in accordance with CSA B55.1. Full credits are applicable to the following building uses: I-2, I-4, R-1, R-2 and also Group E where there are more than eight showers. Partial credits are applicable to *buildings* where all but ground floor show- ers are served where the base energy credit from Section C406.2 is adjusted by Equation 4-21*.*

**Equation 4-21** W10 credit = W10 base energy credit × (showers with drain heat recovery/total showers in building)

**C406.2.4 P01 Energy monitoring.** A project not required to comply with Section C405.13 can achieve energy credits for installing an energy monitoring system that complies with all the requirements of Sections C405.13.1 through C405.13.5.

**C406.2.5 Energy savings in lighting systems.** Projects are permitted to achieve energy credits for increased lighting system performance by meeting the requirements of one of the following:

1. Section C406.2.5.2 L02.
2. Section C406.2.5.3 L03.
3. Section C406.2.5.4 L04.
4. Section C406.2.5.5 L05.
5. Section C406.2.5.6 L06.
6. Any combination of L03, L04, L05 and L06.
7. Any combination of L02, L03 and L04.

**C406.2.5.1 L01 Lighting system performance (reserved).** Reserved for future use.

**C406.2.5.2 L02 High-end trim lighting controls.** Measure credits shall be achieved where qualifying spaces are not less than 50 percent of the project interior floor area exclusive of *dwelling* and *sleeping units*. Qualifying spaces are those where *general lighting* is controlled by *high-end trim* lighting controls complying with the following:

* 1. The calibration adjustment equipment is located for ready access only by authorized personnel.
  2. Lighting controls with ready access for users cannot increase the lighting power above the maximum level estab- lished by the *high-end trim* controls.
  3. Construction documents shall state that maximum light output or power of general lighting in spaces contributing to the qualifying floor area shall be not greater than 85 percent of full power or light output.
  4. *High-end trim* lighting controls shall be tested in accordance with Section C408.3.1.5.

The base credits from Tables C406.2(1) through C406.2(9) shall be prorated as follows:

*HET* × [Base energy credits for C406.2.5.2]/50% where:

*HET* = Floor area of qualifying spaces where *general lighting* is provided with high-end trim lighting controls complying with this section, expressed as a percentage of total interior floor area, excluding *dwelling* and *sleeping units*.

**C406.2.5.3 L03 Increase occupancy sensor.** Lighting controls shall comply with Sections C406.2.5.3.1, C406.2.5.3.2 and C406.2.5.3.3.

**C406.2.5.3.1 Occupant sensor controls.** Occupant sensor controls shall be installed to control lights in the following space types:

* + 1. Food preparation area.
    2. Laboratory.
    3. Elevator lobby.
    4. Pharmacy area.
    5. Vehicular maintenance area.
    6. Workshop.
    7. Recreation room in a facility for the visually impaired.
    8. Exercise area in a fitness center.
    9. Playing area in a fitness center.
    10. Exam/treatment room in a health care facility.
    11. Imaging room in a health care facility.
    12. Physical therapy room in a health care facility.
    13. Library reading area.
    14. Library stacks.
    15. Detailed manufacturing area.
    16. *Equipment room* in a manufacturing facility.
    17. Low-bay area in a manufacturing facility.
    18. Post office sorting area.
    19. Religious fellowship hall.
    20. Hair salon.
    21. Nail salon.
    22. Banking activity area.
    23. Museum restoration room.

**C406.2.5.3.2 Occupant sensor control function.** Occupant sensors in library stacks and laboratories shall comply with Section C405.2.1.2. Occupant sensors in elevator lobbies shall comply with Section C405.2.1.4. All other occupant sensors required by Section C406.2.5.3.1 shall comply with Section C405.2.1.1.

**Exception:** In spaces where an *automatic* shutoff could endanger occupant safety or security, occupant sensor controls shall uniformly reduce lighting power to not more than 20 percent of full power within 10 minutes after all occupants have left the space. Time-switch controls complying with Section C405.2.2.1 shall automatically turn off lights.

**C406.2.5.3.3 Occupant sensor time delay and setpoint.** Occupant sensor controls installed in accordance with Sections C405.2.1.1, C405.2.1.2, C405.2.1.3 and C405.2.1.4 shall automatically turn off lights or reduce lighting power within 10 minutes after all occupants have left the space. Occupant sensor controls installed in accordance with Section C405.2.1.2 shall have an unoccupied setpoint of not greater than 20 percent of full power.

**C406.2.5.4 L04 Increased daylight area.** The total daylight area of the *building* (*DLABLDG*) determined by Equation 4-22 shall be at least 5 percent greater than the typical daylight area (*DLATYP*) from Table C406.2.5.4. Credits for measure L04 shall be deter- mined by Equation 4-23 or Equation 4-24, whichever is less:

**Equation 4-22** *DLABLDG* = *DLZ*/*LFA*

where:

*DLZ* = The total building floor area located within sidelit and toplit daylight zones complying with Section C405.2.4.2 or C405.2.4.3 and provided with daylight responsive controls complying with Section C405.2.4.1, ft 2 or m2.

*LFA* = The total building floor area used to determine the lighting power allowance in Section C405.3.2, ft2 or m2.

**Equation 4-23** *ECDL* = *ECDL*5 × 20 × (*DLABLDG* - *DLATYP*)

where:

*ECDL* = The lesser of actual area of daylight zones in the *building* with continuous daylight dimming, ft2 or m2 and (*GLFA*

× *DLA* ); see Table C406.2.5.4. Daylight zones shall meet the criteria in Sections C405.2.4.2 and C405.2.4.3 for primary sidelit daylight zones, secondary sidelit daylight zones and toplit daylight zones.

*DLATYP* = Typical percent of building area with daylight control (as a fraction) from Table C406.2.5.4.

*ECDL5* = Section C406.2.5.4 L04 base energy credits from Section C406.2.

**Equation 4-24** *ECDL* = *ECDL5* × 20 × (DLAMAX - *DLATYP*)

where:

*ECDL* = The number of credits achieved by this measure.

*ECDL5* = Section C406.2.5.4 L04 base energy credits from Section C406.2 and Tables C406.2(4), C406.2(6), C406.2(7) and C406.2(8).

*DLATYP* = Typical percent of building floor area with daylight control (as a fraction) from Table C406.2.5.4.

*DLAMAX* = Maximum percent of building floor area with daylight control that can be counted for compliance with this measure, from Table C406.2.5.4.

|  |  |  |
| --- | --- | --- |
| **TABLE C406.2.5.4—ADDED DAYLIGHTING PARAMETERS** | | |
| **BUILDING-USE TYPE** | ***DLATYP*** | ***DLAMAX*** |
| Group B; ≤ 5,000 ft2 (460 m2) | 10% | 20% |
| Group B; > 5,000 ft2 (460 m2) | 21% | 31% |
| Group M; with ≤ 1,000 ft2 (900 m2) roof area | 0% | 20% |
| Group M; with > 1,000 ft2 (900 m2) roof area | 60% | 80% |
| Group E; education | 42% | 52% |
| Groups S-1 and S-2; warehouse | 50% | 70% |
| Groups S-1 and S-2; other than warehouse | NA | NA |
| NA = Not Available. | | |

**C406.2.5.5 L05 Residential light control.** In *buildings* with Group R-2 occupancy spaces, interior lighting systems shall comply with the following:

1. In *common areas*, the following space types shall have occupant sensor controls that comply with the requirements of Section C405.2.1.1:
   1. Laundry/washing areas.
   2. Dining areas.
   3. Food preparation areas.
   4. Seating areas.
   5. Exercise areas.
   6. Massage spaces.
2. In *dwelling units*, not less than one receptacle in each living room and each sleeping room shall be controlled by a switch in that room.
3. Lights and switched receptacles in bathrooms and kitchens shall be controlled by an occupant sensor complying with Section C405.2.1.1. All other lights and switched receptacles in each *dwelling unit* shall be controlled by a switch at the main entrance. The switch shall be marked to indicate its function.

**Exception:** Lighting and switched receptacles controlled by an occupant sensor complying with Section C405.2.1.1 are not required to be controlled by the switch at the main entrance.

**C406.2.5.6 L06 Reduced lighting power.** Interior lighting within all *building* areas shall comply with this section.

1. The connected interior lighting power (LP) determined in accordance with Section C405.3.1 shall be 95 percent or less than the interior lighting power allowance (LPA) determined in accordance with Section C405.3.2 using the same method used to comply with Section C405.3. Energy credits shall not be greater than four times the L06 base credit from Section C406.2 and shall be determined using Equation 4-25.
2. All permanently installed lighting serving *dwelling units* and *sleeping units*, including ceiling fan light kits and lighting integrated into range hoods and exhaust fans shall be provided by lamps with an efficacy of not less than 90 lumens per watt or by luminaires that have an efficacy of not less than 65 lumens per watt.

Exceptions:

* 1. Lighting integral to other appliances.
  2. Antimicrobial lighting used for the sole purpose of disinfecting.

**Equation 4-25** *ECLPA* = *EC*5 × 20 × (*LPA* - *LP*)/*LPA*

where:

*ECLPA* = Additional energy credit for lighting power reduction.

*LP* = Connected interior lighting power calculated in accordance with Section C405.3.1, watts.

*LPA* = Interior lighting power allowance calculated in accordance with the requirements of Section C405.3.2, watts.

*EC*5 = L06 base credit from Section C406.2.

**C406.2.6 Efficient equipment credits.** Projects are permitted to achieve energy credits using any combination of Efficient Equip- ment Credits Q01 through Q04.

**C406.2.6.1 Q01 Efficient elevator equipment.** Qualifying elevators in the *building* shall be energy efficiency class A per ISO 25745-2, Table 7. Only *buildings* three or more floors above grade may use this credit. Credits shall be prorated based on Equa- tion 4-26, rounded to the nearest whole credit. Projects with a compliance ratio below 0.5 do not qualify for this credit.

**Equation 4-26** *ECe* = *ECt* × *CRe*

where:

*ECe* = Elevator energy credit achieved for the building.

*ECt* = Q01 base energy credit from applicable Table C406.2(1) through Table C406.2(9).

*CRe* = Compliance ratio = *FA*/*FB*.

*FA* = Sum of floors served by class A elevators.

*FB* = Sum of floors served by all building elevators and escalators.

**C406.2.6.2 Q02 Efficient commercial kitchen equipment.** For *buildings* and spaces designated as Group A-2, or facilities whose primary business type involves the use of a commercial kitchen where at least one gas or electric fryer is installed before the issuance of the certificate of occupancy, all fryers, dishwashers, steam cookers and ovens installed before the issu- ance of the certificate of occupancy shall comply with all of the following:

1. Achieve performance levels in accordance with the equipment specifications listed in Tables C406.2.6.2(1) through C406.2.6.2(4) where rated in accordance with the applicable test procedure.
2. Have associated performance levels listed on the *construction documents* submitted for permitting.

|  |  |  |  |
| --- | --- | --- | --- |
| **TABLE C406.2.6.2(1)—MINIMUM EFFICIENCY REQUIREMENTS: COMMERCIAL FRYERS** | | | |
|  | **HEAVY-LOAD COOKING ENERGY EFFICIENCY** | **IDLE ENERGY RATE** | **TEST PROCEDURE** |
| Standard open deep-fat gas fryers | ≥ 50% | ≤ 9,000 Btu/h | ASTM F1361 |
| Standard open deep-fat electric fryers | ≥ 83% | ≤ 800 watts |
| Large vat open deep-fat gas fryers | ≥ 50% | ≤ 12,000 Btu/h | ASTM F2144 |
| Large vat open deep-fat electric fryers | ≥ 80% | ≤ 1,100 watts |
| For SI: 1 British thermal unit per hour = 0.293 watts. | | | |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **TABLE C406.2.6.2(2)—MINIMUM EFFICIENCY REQUIREMENTS: COMMERCIAL STEAM COOKERS** | | | | |
| **FUEL TYPE** | **PAN CAPACITY** | **COOKING ENERGY EFFICIENCYa** | **IDLE ENERGY RATE** | **TEST PROCEDURE** |
| Electric steam | 3-pan | 50% | 400 watts | ASTM F1484 |
| 4-pan | 50% | 530 watts |
| 5-pan | 50% | 670 watts |
| 6-pan and larger | 50% | 800 watts |
| Gas steam | 3-pan | 38% | 6,250 Btu/h |
| 4-pan | 38% | 8,350 Btu/h |
| 5-pan | 38% | 10,400 Btu/h |
| 6-pan and larger | 38% | 12,500 Btu/h |
| For SI: 1 British thermal unit per hour = 0.293 watts.  a. Cooking energy efficiency is based on heavy-load (potato) cooking capacity. | | | | |

|  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE C406.2.6.2(3)—MINIMUM EFFICIENCY REQUIREMENTS: COMMERCIAL DISHWASHERS** | | | | | | | |
| **MACHINE TYPE** | **HIGH-TEMPERATURE EFFICIENCY REQUIREMENTS** | | | **LOW-TEMPERATURE EFFICIENCY REQUIREMENTS** | | | **TEST PROCEDURE** |
| **Idle Energy Ratea** | **Washing Energy** | **Water Consumptionb** | **Idle Energy Ratea** | **Washing Energy** | **Water Consumptionb** |
| Under counter | ≤ 0.30 kW | ≤ 0.35 kWh/rack | ≤ 0.86 GPR  (≤ 3.3 LPR) | ≤ 0.25 kW | ≤ 0.15  kWh/rack | ≤ 1.19 GPR  ≤ 4.5 LPR | ASTM F1696 ASTM F1920 |
| Stationary single-tank door | ≤ 0.55 kW | ≤ 0.35 kWh/rack | ≤ 0.89 GPR  (≤ 3.4 LPR) | ≤ 0.30 kW | ≤ 0.15  kWh/rack | ≤ 1.18 GPR  ≤ 4.47 LPR |
| Pot, pan and utensil | ≤ 0.90 kW | kWh/rack ≤ 0.55 + 0.05 ×  SFrackc  (≤ 0.55 + 0.0046 × SMrackc) | ≤ 0.58 GPSF  (≤ 2.2 LPSM) | NA | NA | NA |
| Single-tank conveyor | ≤ 1.20 kW | ≤ 0.36 kWh/rack | ≤ 0.70 GPR  (≤ 2.6 LPR) | ≤ 0.85 kW | ≤ 0.16  kWh/rack | ≤ 0.79 GPR  ≤ 3.0 LPR |
| Multiple-tank conveyor | ≤ 1.85 kW | ≤ 0.36 kWh/rack | ≤ 0.54 GPR  (≤ 2.0 LPR) | ≤ 1.00 kW | ≤ 0.22  kWh/rack | ≤ 0.54 GPR  ≤ 2.0 LPR |
| Single-tank flight type | Reported | Reported | GPH ≤ 2.975c +  55.0 (LPH ≤  0.276d + 208) | NA | NA | NA |
| Multiple-tank flight type | Reported | Reported | GPH ≤ 4.96c+  17.00 (LPH ≤  0.461d + 787) | NA | NA | NA |
| 1. Idle results should be measured with the door closed and represent the total idle energy consumed by the machine, including all tank heaters and controls. The most energy- consumptive configuration in the product family shall be selected to test the idle energy rate. Booster heater (internal or external) energy consumption shall be measured and reported separately, if possible, per ASTM F1696 and ASTM F1920, Sections 10.8 and 10.9, respectively. However, if booster energy cannot be measured separately, it will be included in the idle energy rate measurements. 2. GPR = gallons per rack, LPR = liters per rack, GPSF = gallons per square foot of rack, LPSM = liters per square meter of rack, GPH = gallons per hour, c = [maximum conveyor belt speed (feet/minute)] × [conveyor belt width (feet)], LPH = liters per hour, d = [maximum conveyor belt speed (m/minute)] × [conveyor belt width (m)]. 3. Pot, pan and utensil (PPU) washing energy is still in the format kWh/rack when evaluated; SFrack (SMrack) is square feet of rack area (square meters of rack area), the same as in the PPU water consumption metric. | | | | | | | |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **TABLE C406.2.6.2(4)—MINIMUM EFFICIENCY REQUIREMENTS: COMMERCIAL OVENS** | | | | |
| **FUEL TYPE** | **CLASSIFICATION** | **IDLE RATE** | **COOKING ENERGY EFFICIENCY, %** | **TEST PROCEDURE** |
| **Convection Ovens** | | | | |
| Gas | Full-size | ≤ 12,000 Btu/h | ≥ 46 | ASTM F1496 |
| Electric | Half-size | ≤ 1.0 kW | ≥ 71 |
| Electric | Full-size | ≤ 1.60 kW |
| **Combination Ovens** | | | | |
| Gas | Steam mode | ≤ 200 Pa + 6,511 Btu/h | ≥ 41 | ASTM F2861 |
| Convection mode | ≤ 150 Pa + 5,425 Btu/h | ≥ 56 |
| Electric | Steam mode | ≤ 0.133 Pa + 0.6400 kW | ≥ 55 |
| Convection mode | ≤ 0.080 Pa + 0.4989 kW | ≥ 76 |
| **Rack Ovens** | | | | |
| Gas | Single | ≤ 25,000 Btu/h | ≥ 48 | ASTM F2093 |
| Double | ≤ 30,000 Btu/h | ≥ 52 |
| For SI: 1 British thermal unit per hour = 0.293 watts.  a. P = Pan capacity: the number of steam table pans the combination oven is able to accommodate in accordance with ASTM F1495. | | | | |

**C406.2.6.3 Q03 Efficient residential kitchen equipment.** For projects with Group R-1 and R-2 occupancies, energy credits shall be achieved where all dishwashers, refrigerators and freezers comply with all of the following:

1. Achieve the Energy Star Most Efficient 2021 label in accordance with the specifications current as of:
   1. Refrigerators and freezers 5.0, 9/15/2014.
   2. Dishwashers 6.0, 1/29/2016.
2. Be installed before the issuance of the certificate of occupancy.

For Group R-1 where only some guestrooms are equipped with both refrigerators and dishwashers, the table credits shall be prorated as follows:

**Equation 4-27** [Section C406.2 base credits] × [floor area of guestrooms with kitchens]/[total guestroom floor area]

**C406.2.6.4 Q04 Fault detection and diagnostics system.** A project not required to comply with Section C403.2.3 can achieve energy credits for installing a fault detection and diagnostics system to monitor the HVAC system’s performance and automat- ically identify faults. The installed system shall comply with Items 1 through 6 in Section C403.2.3.

**C406.3 Renewable and load management credits achieved.** Renewable energy and load management measures shall achieve credits as follows:

1. General measure requirements. Credits are achieved for measures installed in the *building* that comply with Sections C406.3.1 through C406.3.8.
2. Achieved credits are determined as follows:
   1. Measure credits achieved shall be determined in one of two ways, depending on the measure:
      1. The measure credit shall be the base credit listed by occupancy group and *climate zone* for the measure in Tables C406.3(1) through C406.3(9) where no adjustment factor or formula is shown in the description of the measure in Section C406.3.
      2. The measure credit shall be the base energy credit for the measure adjusted by a factor or formula as stated in the description of the measure in Section C406.3. Where adjustments are applied, each energy credit shall be rounded to the nearest whole number.
   2. Load management and renewable credits achieved for the project shall be the sum of credits for individual measures included in the project. Credits are available for the measures listed in this section.
   3. Where a project contains multiple building use groups, credits achieved for each building use group shall be summed and then weighted by the gross floor area of each building use group to determine the weighted-average project energy credits achieved.
3. Load management control requirements. The load management measures in Sections C406.3.2 (G01) through C406.3.7 (G06) require load management control sequences that are capable of and configured to automatically provide the load management operation specified based on indication of a peak period related to high short-term electric prices, grid condi- tion or peak building load. Such a peak period shall, where possible, be initiated by a *demand response signal* from the controlling entity, such as a utility or service operator. Where communications are disabled or unavailable, all demand- responsive controls shall continue backup demand response based on a local schedule or building-demand monitoring. The local building schedule shall be adjustable without programming and reflect the electric rate peak period dates and times. The load management control sequences shall be activated for peak period control by one of the following:
   1. A certified OpenADR 2.0a or OpenADR 2.0b Virtual End Node (VEN), as specified under Clause 11, Conformance, in the applicable OpenADR 2.0 Specification.
   2. A device certified by the manufacturer as being capable of responding to a *demand response signal* from a certi- fied OpenADR 2.0b VEN by automatically implementing the control functions requested by the VEN for the equipment it controls.
   3. The physical configuration and communication protocol of ANSI/CTA-2045-A or ANSI/CTA-2045-B.
   4. For air conditioners and heat pumps with two or more stages of control and cooling capacity of less than 65,000 Btu/h (19 kW), *thermostats* with a *demand responsive control* that complies with the communication and perfor- mance requirements of AHRI 1380.
   5. A device that complies with IEC 62746-10-1, an international standard for the open automated demand response system interface between the appliance, system, or energy management system and the controlling entity.
   6. An interface that complies with the communication protocol required by a controlling entity to participate in an automated demand response program.
   7. Where the controlling entity does not have a *demand response signal* available for the *building* type and size, local load management control shall be provided based on either:
      1. *Building* demand management controls that monitor *building* electrical demand and initiate controls to minimize monthly or peak time period demand charges.
      2. A local *building* schedule that reflects the electric rate peak period dates and times where *buildings*

are less than 25,000 gross square feet (2322 m2).

In this case, a binary input to the control system shall be provided that activates the demand response sequence.

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE C406.3(1)—RENEWABLE AND LOAD MANAGEMENT CREDITS FOR GROUP R-2, R-4 AND I-1 OCCUPANCIES** | | | | | | | | | | | | | | | | | | | | | |
| **ID** | **ENERGY CREDIT ABBREVIATED TITLE** | **SECTION** | **CLIMATE ZONE** | | | | | | | | | | | | | | | | | | |
| **0A** | **0B** | **1A** | **1B** | **2A** | **2B** | **3A** | **3B** | **3C** | **4A** | **4B** | **4C** | **5A** | **5B** | **5C** | **6A** | **6B** | **7** | **8** |
| R01 | Renewable energy | C406.3.1 | 9 | 15 | 11 | 17 | 18 | 20 | 19 | 21 | 13 | 10 | 13 | 9 | 9 | 11 | 10 | 9 | 10 | 9 | 7 |
| G01 | Lighting load management | C406.3.2 | 16 | 7 | 9 | 12 | 12 | 16 | 11 | 14 | 12 | 11 | 16 | 14 | 8 | 11 | 14 | 5 | 7 | 7 | 11 |
| G02 | HVAC load management | C406.3.3 | 42 | 41 | 21 | 35 | 23 | 37 | 30 | 28 | 28 | 17 | 33 | 24 | 20 | 22 | 23 | 10 | 13 | 15 | 17 |
| G03 | Automated shading | C406.3.4 | 11 | x | 7 | 18 | 10 | 13 | 5 | 13 | 12 | 2 | 14 | 7 | 10 | 13 | 11 | 1 | 8 | 8 | 16 |
| G04 | Electric energy storage | C406.3.5 | 10 | 10 | 10 | 11 | 10 | 13 | 13 | 14 | 17 | 16 | 13 | 17 | 14 | 13 | 17 | 14 | 14 | 14 | 15 |
| G05 | Cooling energy storage | C406.3.6 | 28 | 6 | 31 | 13 | 22 | 21 | 21 | 37 | 11 | 12 | 22 | 11 | 9 | 17 | 9 | 7 | 17 | 2 | 3 |
| G06 | SHW energy storage | C406.3.7 | 17 | 17 | 19 | 18 | 19 | 19 | 20 | 20 | 22 | 19 | 19 | 21 | 19 | 19 | 20 | 18 | 19 | 18 | 17 |
| G07 | Building thermal mass | C406.3.8 | 7 | 2 | 11 | 5 | 16 | 28 | 22 | 27 | 60 | 19 | 43 | 46 | 32 | 58 | 37 | 27 | 45 | 40 | 19 |
| HVAC = Heating, Ventilation and Air Conditioning; SHW = Service Hot Water. x = Credits excluded from this building use type and climate zone. | | | | | | | | | | | | | | | | | | | | | |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE C406.3(2)—RENEWABLE AND LOAD MANAGEMENT CREDITS FOR GROUP I-2 OCCUPANCIES** | | | | | | | | | | | | | | | | | | | | | |
| **ID** | **ENERGY CREDIT ABBREVIATED TITLE** | **SECTION** | **CLIMATE ZONE** | | | | | | | | | | | | | | | | | | |
| **0A** | **0B** | **1A** | **1B** | **2A** | **2B** | **3A** | **3B** | **3C** | **4A** | **4B** | **4C** | **5A** | **5B** | **5C** | **6A** | **6B** | **7** | **8** |
| R01 | Renewable energy | C406.3.1 | 6 | 6 | 6 | 6 | 6 | 8 | 7 | 9 | 8 | 6 | 8 | 6 | 6 | 7 | 7 | 6 | 7 | 5 | 4 |
| G01 | Lighting load management | C406.3.2 | 11 | 12 | 13 | 13 | 13 | 12 | 12 | 12 | 6 | 13 | 16 | 12 | 13 | 14 | 15 | 14 | 14 | 12 | 12 |
| G02 | HVAC load management | C406.3.3 | 10 | 11 | 10 | 10 | 8 | 21 | 10 | 10 | 13 | 11 | 18 | 11 | 12 | 14 | 13 | 12 | 11 | 9 | 7 |
| G03 | Automated shading | C406.3.4 | 1 | 1 | 1 | 1 | x | x | x | 1 | x | x | 2 | x | x | 2 | x | x | 1 | 1 | x |
| G04 | Electric energy storage | C406.3.5 | 13 | 13 | 13 | 13 | 14 | 15 | 14 | 15 | 15 | 14 | 15 | 15 | 14 | 15 | 15 | 13 | 14 | 13 | 12 |
| G05 | Cooling energy storage | C406.3.6 | 25 | 6 | 33 | 14 | 25 | 19 | 27 | 37 | 27 | 16 | 22 | 19 | 14 | 18 | 11 | 11 | 20 | 2 | 3 |
| G06 | SHW energy storage | C406.3.7 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 |
| G07 | Building thermal mass | C406.3.8 | 6 | 2 | 10 | 4 | 15 | 25 | 20 | 24 | 57 | 18 | 39 | 44 | 31 | 53 | 33 | 25 | 40 | 34 | 14 |
| HVAC = Heating, Ventilation and Air Conditioning; SHW = Service Hot Water. x = Credits excluded from this building use type and climate zone*.* | | | | | | | | | | | | | | | | | | | | | |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE C406.3(3)—RENEWABLE AND LOAD MANAGEMENT CREDITS FOR GROUP R-1 OCCUPANCIES** | | | | | | | | | | | | | | | | | | | | | |
| **ID** | **ENERGY CREDIT ABBREVIATED TITLE** | **SECTION** | **CLIMATE ZONE** | | | | | | | | | | | | | | | | | | |
| **0A** | **0B** | **1A** | **1B** | **2A** | **2B** | **3A** | **3B** | **3C** | **4A** | **4B** | **4C** | **5A** | **5B** | **5C** | **6A** | **6B** | **7** | **8** |
| R01 | Renewable energy | C406.3.1 | 9 | 8 | 12 | 9 | 11 | 11 | 10 | 12 | 13 | 9 | 12 | 8 | 9 | 11 | 9 | 8 | 9 | 7 | 5 |
| G01 | Lighting load management | C406.3.2 | 12 | 12 | 11 | 12 | 12 | 14 | 14 | 13 | 15 | 14 | 13 | 11 | 10 | 11 | 14 | 9 | 11 | 8 | 8 |
| G02 | HVAC load management | C406.3.3 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| G03 | Automated shading | C406.3.4 | 2 | 2 | 2 | 3 | 1 | 2 | 3 | 2 | 4 | 3 | 2 | 1 | 1 | 1 | 3 | 1 | 2 | 1 | 1 |
| G04 | Electric energy storage | C406.3.5 | 9 | 9 | 10 | 10 | 9 | 13 | 13 | 15 | 13 | 14 | 13 | 14 | 14 | 12 | 16 | 13 | 12 | 12 | 13 |
| G05 | Cooling energy storage | C406.3.6 | 31 | 7 | 38 | 17 | 29 | 24 | 31 | 44 | 26 | 18 | 26 | 16 | 15 | 21 | 11 | 12 | 24 | 2 | 4 |
| G06 | SHW energy storage | C406.3.7 | 25 | 25 | 28 | 26 | 28 | 29 | 29 | 30 | 31 | 29 | 30 | 31 | 28 | 29 | 31 | 26 | 28 | 25 | 24 |
| G07 | Building thermal mass | C406.3.8 | 6 | 1 | 10 | 4 | 14 | 24 | 19 | 23 | 53 | 17 | 38 | 41 | 30 | 52 | 33 | 26 | 42 | 37 | 17 |
| HVAC = Heating, Ventilation and Air Conditioning; SHW = Service Hot Water. x = Credits excluded from this building use type and climate zone*.* | | | | | | | | | | | | | | | | | | | | | |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE C406.3(4)—RENEWABLE AND LOAD MANAGEMENT CREDITS FOR GROUP B OCCUPANCIES** | | | | | | | | | | | | | | | | | | | | | |
| **ID** | **ENERGY CREDIT ABBREVIATED TITLE** | **SECTION** | **CLIMATE ZONE** | | | | | | | | | | | | | | | | | | |
| **0A** | **0B** | **1A** | **1B** | **2A** | **2B** | **3A** | **3B** | **3C** | **4A** | **4B** | **4C** | **5A** | **5B** | **5C** | **6A** | **6B** | **7** | **8** |
| R01 | Renewable energy | C406.3.1 | 14 | 14 | 17 | 15 | 17 | 19 | 18 | 22 | 24 | 17 | 22 | 16 | 14 | 18 | 18 | 14 | 17 | 14 | 11 |
| G01 | Lighting load management | C406.3.2 | 10 | 11 | 11 | 12 | 11 | 11 | 11 | 12 | 9 | 10 | 11 | 10 | 10 | 11 | 10 | 10 | 11 | 10 | 9 |
| G02 | HVAC load management | C406.3.3 | x | 10 | 10 | 9 | 9 | 3 | 8 | 12 | 7 | 12 | 8 | 11 | 9 | 10 | 12 | 8 | 9 | 10 | 2 |
| G03 | Automated shading | C406.3.4 | 4 | 7 | 7 | 8 | 7 | 8 | 5 | 6 | 6 | 4 | 6 | 5 | 4 | 5 | 5 | 5 | 5 | 4 | 7 |
| G04 | Electric energy storage | C406.3.5 | 14 | 15 | 14 | 14 | 16 | 16 | 17 | 16 | 18 | 17 | 16 | 18 | 17 | 17 | 18 | 16 | 15 | 17 | 18 |
| G05 | Cooling energy storage | C406.3.6 | 28 | 7 | 36 | 16 | 27 | 24 | 28 | 45 | 27 | 17 | 27 | 15 | 15 | 20 | 9 | 12 | 25 | 2 | 4 |
| G06 | SHW energy storage | C406.3.7 | 5 | 5 | 6 | 6 | 6 | 6 | 7 | 7 | 8 | 7 | 7 | 7 | 7 | 7 | 8 | 6 | 7 | 6 | 6 |
| G07 | Building thermal mass | C406.3.8 | 3 | 1 | 5 | 2 | 6 | 9 | 6 | 7 | 14 | 4 | 11 | 8 | 9 | 15 | 5 | 8 | 12 | 15 | 7 |
| HVAC = Heating, Ventilation and Air Conditioning; SHW = Service Hot Water. x = Credits excluded from this building use type and climate zone*.* | | | | | | | | | | | | | | | | | | | | | |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE C406.3(5)—RENEWABLE AND LOAD MANAGEMENT CREDITS FOR A-2 OCCUPANCIES** | | | | | | | | | | | | | | | | | | | | | |
| **ID** | **ENERGY CREDIT ABBREVIATED TITLE** | **SECTION** | **CLIMATE ZONE** | | | | | | | | | | | | | | | | | | |
| **0A** | **0B** | **1A** | **1B** | **2A** | **2B** | **3A** | **3B** | **3C** | **4A** | **4B** | **4C** | **5A** | **5B** | **5C** | **6A** | **6B** | **7** | **8** |
| R01 | Renewable energy | C406.3.1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 4 | 2 | 3 | 2 | 2 | 3 | 2 | 2 | 2 | 2 | 1 |
| G01 | Lighting load management | C406.3.2 | 4 | 4 | 5 | 5 | 4 | 5 | 5 | 5 | 5 | 4 | 5 | 5 | 4 | 4 | 5 | 4 | 5 | 4 | 1 |
| G02 | HVAC load management | C406.3.3 | 32 | 26 | 37 | 28 | 31 | 26 | 27 | 22 | 23 | 20 | 17 | 14 | 19 | 14 | 10 | 16 | 14 | 14 | 1 |
| G03 | Automated shading | C406.3.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| G04 | Electric energy storage | C406.3.5 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 4 | 4 | 4 | 4 | 3 | 4 | 4 | 4 | 3 | 3 | 2 |
| G05 | Cooling energy storage | C406.3.6 | 15 | 4 | 17 | 8 | 12 | 10 | 10 | 16 | 6 | 5 | 7 | 3 | 3 | 4 | 1 | 2 | 4 | x | x |
| G06 | SHW energy storage | C406.3.7 | 13 | 13 | 15 | 14 | 15 | 16 | 16 | 17 | 19 | 16 | 17 | 19 | 16 | 17 | 18 | 15 | 16 | 14 | 13 |
| G07 | Building thermal mass | C406.3.8 | 3 | 1 | 5 | 2 | 7 | 12 | 8 | 10 | 21 | 6 | 15 | 14 | 8 | 18 | 10 | 6 | 12 | 8 | 3 |
| HVAC = Heating, Ventilation and Air Conditioning; SHW = Service Hot Water. x = Credits excluded from this building use type and climate zone*.* | | | | | | | | | | | | | | | | | | | | | |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE C406.3(6)—RENEWABLE AND LOAD MANAGEMENT CREDITS FOR GROUP M OCCUPANCIES** | | | | | | | | | | | | | | | | | | | | | |
| **ID** | **ENERGY CREDIT ABBREVIATED TITLE** | **SECTION** | **CLIMATE ZONE** | | | | | | | | | | | | | | | | | | |
| **0A** | **0B** | **1A** | **1B** | **2A** | **2B** | **3A** | **3B** | **3C** | **4A** | **4B** | **4C** | **5A** | **5B** | **5C** | **6A** | **6B** | **7** | **8** |
| R01 | Renewable energy | C406.3.1 | 8 | 8 | 12 | 9 | 11 | 12 | 12 | 17 | 17 | 11 | 13 | 9 | 10 | 11 | 10 | 9 | 10 | 9 | 6 |
| G01 | Lighting load management | C406.3.2 | 16 | 16 | 18 | 19 | 17 | 19 | 19 | 21 | 17 | 18 | 21 | 21 | 18 | 21 | 22 | 18 | 22 | 18 | 16 |
| G02 | HVAC load management | C406.3.3 | x | 15 | 16 | 15 | 15 | 6 | 15 | 21 | 13 | 23 | 15 | 23 | 17 | 19 | 26 | 14 | 17 | 18 | 3 |
| G03 | Automated shading | C406.3.4 | 7 | 11 | 11 | 12 | 11 | 13 | 10 | 11 | 11 | 7 | 11 | 11 | 8 | 10 | 11 | 8 | 9 | 8 | 12 |
| G04 | Electric energy storage | C406.3.5 | 6 | 10 | 8 | 10 | 11 | 12 | 11 | 10 | 14 | 11 | 10 | 12 | 10 | 11 | 12 | 11 | 9 | 10 | 8 |
| G05 | Cooling energy storage | C406.3.6 | 40 | 9 | 51 | 22 | 35 | 31 | 34 | 53 | 21 | 17 | 28 | 10 | 11 | 19 | 4 | 9 | 18 | 2 | 2 |
| G06 | SHW energy storage | C406.3.7 | 3 | 3 | 4 | 3 | 4 | 4 | 4 | 4 | 5 | 4 | 4 | 5 | 4 | 4 | 5 | 4 | 4 | 4 | 3 |
| G07 | Building thermal mass | C406.3.8 | 5 | 1 | 6 | 3 | 8 | 12 | 10 | 10 | 20 | 7 | 17 | 15 | 14 | 24 | 10 | 13 | 20 | 24 | 12 |
| HVAC = Heating, Ventilation and Air Conditioning; SHW = Service Hot Water. x = Credits excluded from this building use type and climate zone*.* | | | | | | | | | | | | | | | | | | | | | |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE C406.3(7)—RENEWABLE AND LOAD MANAGEMENT CREDITS FOR GROUP E OCCUPANCIES** | | | | | | | | | | | | | | | | | | | | | |
| **ID** | **ENERGY CREDIT ABBREVIATED TITLE** | **SECTION** | **CLIMATE ZONE** | | | | | | | | | | | | | | | | | | |
| **0A** | **0B** | **1A** | **1B** | **2A** | **2B** | **3A** | **3B** | **3C** | **4A** | **4B** | **4C** | **5A** | **5B** | **5C** | **6A** | **6B** | **7** | **8** |
| R01 | Renewable energy | C406.3.1 | 10 | 11 | 13 | 12 | 13 | 16 | 15 | 21 | 22 | 15 | 19 | 15 | 14 | 17 | 16 | 13 | 16 | 12 | 10 |
| G01 | Lighting load management | C406.3.2 | 7 | 12 | 12 | 13 | 13 | 15 | 14 | 16 | 13 | 12 | 16 | 16 | 10 | 14 | 18 | 16 | 13 | 14 | 14 |
| G02 | HVAC load management | C406.3.3 | 18 | 22 | 32 | 23 | 25 | 31 | 26 | 26 | 20 | 23 | 31 | 24 | 20 | 31 | 12 | 18 | 27 | 16 | 9 |
| G03 | Automated shading | C406.3.4 | 7 | 13 | 16 | 12 | 18 | 17 | 17 | 18 | 13 | 12 | 17 | 17 | 10 | 15 | 13 | 14 | 10 | 16 | 17 |
| G04 | Electric energy storage | C406.3.5 | 16 | 16 | 18 | 17 | 19 | 21 | 21 | 23 | 26 | 22 | 24 | 24 | 23 | 24 | 24 | 20 | 22 | 19 | 19 |
| G05 | Cooling energy storage | C406.3.6 | 36 | 9 | 46 | 21 | 36 | 32 | 39 | 62 | 39 | 24 | 37 | 22 | 20 | 28 | 13 | 16 | 31 | 3 | 4 |
| G06 | SHW energy storage | C406.3.7 | 5 | 5 | 6 | 5 | 6 | 6 | 7 | 7 | 8 | 7 | 7 | 8 | 7 | 7 | 8 | 7 | 7 | 7 | 6 |
| G07 | Building thermal mass | C406.3.8 | 7 | 2 | 11 | 5 | 17 | 28 | 23 | 27 | 63 | 21 | 44 | 48 | 37 | 60 | 38 | 31 | 50 | 47 | 21 |
| HVAC = Heating, Ventilation and Air Conditioning; SHW = Service Hot Water. x = Credits excluded from this building use type and climate zone*.* | | | | | | | | | | | | | | | | | | | | | |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE C406.3(8)—RENEWABLE AND LOAD MANAGMENT CREDITS FOR GROUP S-1 AND S-2 OCCUPANCIES** | | | | | | | | | | | | | | | | | | | | | |
| **ID** | **ENERGY CREDIT ABBREVIATED TITLE** | **SECTION** | **CLIMATE ZONE** | | | | | | | | | | | | | | | | | | |
| **0A** | **0B** | **1A** | **1B** | **2A** | **2B** | **3A** | **3B** | **3C** | **4A** | **4B** | **4C** | **5A** | **5B** | **5C** | **6A** | **6B** | **7** | **8** |
| R01 | Renewable energy | C406.3.1 | 38 | 37 | 55 | 45 | 53 | 53 | 49 | 58 | 66 | 36 | 56 | 38 | 29 | 41 | 36 | 24 | 32 | 23 | 16 |
| G01 | Lighting load management | C406.3.2 | 13 | 26 | 32 | 28 | 32 | 35 | 36 | 33 | 36 | 31 | 27 | 37 | 32 | 23 | 28 | 36 | 22 | 25 | 22 |
| G02 | HVAC load management | C406.3.3 | 18 | 46 | 37 | 37 | 28 | 36 | 29 | 26 | 22 | 23 | 17 | 12 | 16 | 13 | 5 | 14 | 8 | 10 | 3 |
| G03 | Automated shading | C406.3.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |
| G04 | Electric energy storage | C406.3.5 | 40 | 40 | 47 | 41 | 47 | 44 | 40 | 44 | 42 | 30 | 38 | 31 | 21 | 31 | 26 | 24 | 29 | 23 | 21 |
| G05 | Cooling energy storage | C406.3.6 | 20 | 5 | 21 | 11 | 14 | 14 | 11 | 21 | 5 | 5 | 9 | 2 | 2 | 5 | 1 | 1 | 3 | x | x |
| G06 | SHW energy storage | C406.3.7 | 3 | 3 | 3 | 3 | 4 | 3 | 4 | 4 | 4 | 3 | 4 | 4 | 3 | 3 | 4 | 2 | 2 | 2 | 2 |
| G07 | Building thermal mass | C406.3.8 | 7 | 2 | 12 | 5 | 17 | 29 | 23 | 28 | 66 | 18 | 44 | 47 | 28 | 56 | 37 | 20 | 39 | 29 | 13 |
| HVAC = Heating, Ventilation and Air Conditioning; SHW = Service Hot Water.  x indicates measure is not available for building occupancy in that climate zone*.* | | | | | | | | | | | | | | | | | | | | | |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE C406.3(9)—RENEWABLE AND LOAD MANAGEMENT CREDITS FOR OTHERa OCCUPANCIES** | | | | | | | | | | | | | | | | | | | | | |
| **ID** | **ENERGY CREDIT ABBREVIATED TITLE** | **SECTION** | **CLIMATE ZONE** | | | | | | | | | | | | | | | | | | |
| **0A** | **0B** | **1A** | **1B** | **2A** | **2B** | **3A** | **3B** | **3C** | **4A** | **4B** | **4C** | **5A** | **5B** | **5C** | **6A** | **6B** | **7** | **8** |
| R01 | Renewable energy | C406.3.1 | 12 | 13 | 16 | 14 | 16 | 18 | 17 | 20 | 21 | 13 | 18 | 13 | 12 | 15 | 14 | 11 | 13 | 10 | 8 |
| G01 | Lighting load management | C406.3.2 | 11 | 13 | 14 | 14 | 14 | 16 | 15 | 16 | 14 | 14 | 16 | 16 | 13 | 14 | 16 | 14 | 13 | 12 | 12 |
| G02 | HVAC load management | C406.3.3 | 24 | 24 | 23 | 22 | 20 | 23 | 21 | 21 | 18 | 18 | 20 | 17 | 16 | 18 | 14 | 13 | 14 | 13 | 6 |
| G03 | Automated shading | C406.3.4 | 5 | 6 | 7 | 9 | 8 | 9 | 7 | 9 | 8 | 5 | 9 | 7 | 5 | 8 | 7 | 5 | 6 | 6 | 9 |
| G04 | Electric energy storage | C406.3.5 | 14 | 15 | 16 | 15 | 16 | 17 | 17 | 18 | 19 | 16 | 17 | 17 | 15 | 16 | 17 | 14 | 15 | 14 | 14 |
| G05 | Cooling energy storage | C406.3.6 | 28 | 7 | 34 | 15 | 25 | 22 | 25 | 39 | 20 | 14 | 22 | 12 | 11 | 17 | 7 | 9 | 18 | 2 | 3 |
| G06 | SHW energy storage | C406.3.7 | 9 | 9 | 11 | 10 | 11 | 11 | 11 | 12 | 13 | 11 | 12 | 13 | 11 | 11 | 12 | 10 | 11 | 10 | 9 |
| G07 | Building thermal mass | C406.3.8 | 6 | 2 | 9 | 4 | 13 | 21 | 16 | 20 | 44 | 14 | 31 | 33 | 24 | 42 | 25 | 20 | 33 | 29 | 13 |
| HVAC = Heating, Ventilation and Air Conditioning; SHW = Service Hot Water.  a. Other occupancy groups include all Groups except for Groups A-2, B, E, I, M and R. | | | | | | | | | | | | | | | | | | | | | |

**C406.3.1 R01 Renewable energy.** Projects installing on-site renewable energy systems with a capacity of at least 0.1 watts per gross square foot (1.08 W/m2) of *building* area or securing off-site renewable energy shall achieve energy credits for this measure calculated as follows:

**Equation 4-28** *ECR* = *EC*0.1 × (*Rt* + *Roff* - *Rex*)/(0.1 × *PGFA*) where:

*ECR* = Section C406.3.1 R01 energy credits achieved for this project.

*EC0.1* = Section C406.3.1 R01 base credits from Tables C406.3(1) through C406.3(9).

*Rt* = Actual total rating of on-site renewable energy systems (W).

*Roff* = Actual total equivalent rating of off-site renewable energy contracts (W), calculated as follows:

*Roff* = *TRE*/(*REN* × 20)

where:

*TRE* = Total off-site renewable electrical energy in kilowatt-hours (kWh) that is procured in accordance with Sections C405.15.2.1 through C405.15.4.

*REN* = Annual off-site renewable electrical energy from Table C405.15.2, in units of kilowatt-hours per watt of array capacity.

*Rex* = Rating (W) of renewable energy resources capacity excluded from credit calculated as follows:

*Rex* = *RRr + RRx + RRc*

where:

*RRr* = Rating of on-site renewable energy systems required by Section C405.15.1, without exception (W).

*RRx* = Rating of renewable energy resources used to meet any exceptions of this code (W).

*RRc =* Rating of renewable energy resources used to achieve other energy credits in Section C406 (W).

*PGFA* = Project gross floor area, ft2. Where renewable requirements, exceptions or credits are expressed in annual kWh or Btu rather than watts of output capacity, they shall be converted as 3413 Btu = 1 kWh and converted to W equivalent capacity as follows:

*RRw* = Actual total equivalent rating of renewable energy capacity (W), calculated as follows:

*RRw* = *TREx* /(*REN* × *PGFA*)

where:

*TREx* = Total renewable energy in kilowatt-hours (kWh) that is excluded from R01 energy credits.

**C406.3.2 G01 Lighting load management.** A project not required to comply with Section C405.2.8 can achieve energy credits for installing demand-responsive lighting controls for interior *general lighting* that comply with Section C405.2.8.1. The demand- responsive lighting controls shall automatically reduce the light output or power of controlled lighting to not more than 80

percent of full output, or 80 percent of the *high-end trim* setpoint, whichever is less. Energy credits can be earned where demand- responsive lighting controls are installed for the following:

1. Not less than 10 percent of the interior floor area in Group R or I occupancies.
2. Not less than 50 percent of the interior floor area in all other occupancies.

G01 credits shall be prorated using Equation 4-29 with not more than 75 percent of the interior floor area being counted.

**Equation 4-29** [interior floor area with lighting load management, %] × [table credits for Section C406.3.2]/75%

**C406.3.3 G02 HVAC load management.** *Automatic* load management controls shall be configured as follows:

1. Cooling temperature shift: Where electric cooling is in use, controls shall gradually increase the cooling setpoint by at least 3°F (1.7°C) over a minimum of 3 hours or reduce effective cooling capacity to 60 percent of installed capacity during the peak period or adjust the cooling temperature setpoint as described in Section C403.6.1.
2. Heating temperature shift: Where electric heating is in use, controls shall gradually decrease the heating setpoint by at least 3°F (1.7°C) over a minimum of 3 hours or reduce effective heating capacity to 60 percent of installed capacity during the peak period or adjust the heating temperature setpoint as described in Section C403.6.1.
3. Ventilation shift: Where HVAC systems serve multiple zones and have less than 70 percent outdoor air required, include controls that provide excess outdoor air preceding the peak period and reduce outdoor air by at least 30 percent during the peak period, in accordance with ASHRAE Standard 62.1 Section 6.2.5.2 or provisions for approved engineering analy- sis in Section 403.3.1.1 of the International Mechanical Code.

Credits achieved for measure G02 shall be calculated as follows:

**Equation 4-30** *EC*G02\_*ach* = *EC*G02\_base × *EC*G02\_*adj*

where:

*EC*G02\_*ach* = Demand responsive control credit achieved for project.

*EC*G02\_*base* = G02 Base energy credit from Section C406.3.

*EC*G02\_*adj* = Energy credit adjustment factor from Table C406.3.3.

|  |  |  |  |
| --- | --- | --- | --- |
| **TABLE C406.3.3—ENERGY CREDIT ADJUSTMENT BASED ON USE OF VENTILATION SHIFT OR DEMAND RESPONSE** | | | |
| **DEMAND RESPONSE SIGNAL AVAILABLEa** | **DEMAND RESPONSE REQUIRED BY SECTION C403.4.6.1b** | **INCLUDES VENTILATION SHIFTc** | ***EC*G02\_*adj*** |
| No | No | Yes | 100% |
| No | Yes | Yes | 80% |
| Yes | No | Yes | 80% |
| Yes | Yes | Yes | 40% |
| No | No | No | 70% |
| No | Yes | No | 50% |
| Yes | No | No | 50% |
| Yes | Yes | No | 0% |
| 1. “Demand Response Signal Available” is “Yes” where a controlling entity other than the owner makes a demand response signal available to the building. 2. Where the exception is invoked in Section C403.4.6.1 for buildings that comply with Load Management measure G02, then “Demand Response Required” is “Yes.” 3. Ventilation shift controls in accordance with Section C406.3.3, Item 3. | | | |

**C406.3.4 G03 Automated shading load management.** Where *fenestration* on east, south and west exposures is greater than 20 percent of the wall area, load management credits shall be achieved as follows:

1. *Automatic* exterior shading devices or *dynamic glazing* that is capable of reducing solar gain through sunlit *fenestration* by not less than 50 percent when fully closed shall receive the full credits in Tables C406.3(1) through C406.3(9). The exterior shades shall have fully open and fully closed *solar heat gain coefficient* (SHGC) determined in accordance with AERC 1.
2. *Automatic* interior shading devices with a solar reflectance of not less than 0.50 for the surface facing the *fenestration*

shall receive 40 percent of the credits in Tables C406.3(1) through C406.3(9).

1. All shading devices, *dynamic glazing* or shading attachments shall:
   1. Provide not less than 90 percent coverage of the total *fenestration* on east, south and west exposures in the *building* to achieve the credits determined in Item 1 or 2. Alternatively, provide not less than 70 percent cover- age of the total *fenestration* on the south and west exposures in the *building* to achieve 50 percent of the credits determined in Item 1 or 2.
   2. Be automatically controlled and shall modulate in multiple steps or continuously the amount of solar gain and light transmitted into the space in response to peak periods and either daylight levels or solar intensity.
   3. Include a *manual* override located in the same *enclosed space* as the shaded vertical *fenestration* that shall override operation of *automatic* controls for not longer than 4 hours. Such override shall be locked out during peak periods.

For this section, directional exposures shall exclude *fenestration* that has an orientation deviating by more than 45 degrees of facing the cardinal direction. In the southern hemisphere, where the south exposure is referred to, it shall be replaced by the north exposure.

**C406.3.5 G04 Electric energy storage.** Electric storage devices shall be charged and discharged by *automatic* load management controls to store energy during nonpeak periods and use stored energy during peak periods to reduce *building* demand. Electric storage devices shall have a minimum capacity of 1.5 watt-hours per square foot (Wh/ft2) (16 Wh/m2) of gross *building* area. Base credits in Tables C406.3(1) through C406.3(9) are based on installed electric storage of 5 Wh/ft2 (54 Wh/m2) and shall be prorated for actual installed storage capacity between 1.5 and 15 Wh/ft2 (16 to 161 Wh/m2), as follows:

**Equation 4-31** [installed electric storage capacity, Wh/ft2 (Wh/m2)]/5(54) × [table credits for Section C406.3.5]

Larger energy storage shall be permitted; however, credits are limited to the range of 1.5 to 15 Wh/ft2 (16 to 161 Wh/m2).

**C406.3.6 G05 Cooling energy storage.** *Automatic* load management controls shall be capable of activating ice or chilled water storage equipment to reduce demand during summer peak periods. Storage tank standby loss shall be demonstrated through analysis to be not more than 2 percent of storage capacity over a 24-hour period for the cooling design day. Base credits in Section C406.3 are based on storage capacity of the design peak hour cooling load with a 1.15 sizing factor. Credits shall be prorated for installed storage systems sized between 0.5 and 4.0 times the design day peak hour cooling load, rounded to the nearest whole credit. Larger storage shall be permitted but the associated credits are limited to the range provided in this section. Energy credits shall be determined as follows:

**Equation 4-32** *ECS* = *EC*1.0 × (1.44 × *SR* + 0.71)/2.15

where:

*ECs* = Cooling storage credit achieved for project.

*EC*1.0 = G05 base energy credit for building use type and climate zone based on 1.0 ton-hours storage per design day ton (kWh/kW) of cooling load.

*SR* = Storage ratio in ton-hours storage per design day ton (kWh/kW) of cooling load where 0.5 ≤ *SR* ≤ 4.0.

**C406.3.7 G06 Service hot water energy storage.** Where service hot water (SHW) is heated by electricity, *automatic* load management controls complying with ANSI/CTA-2045-B shall preheat stored SHW before the peak period and suspend electric water heating during the peak period. Storage capacity shall be provided by either:

1. Preheating water above 140°F (60°C) delivery temperature with at least 1.34 kWh of energy storage per kW of water-heat- ing capacity. Tempering valves shall be provided at the water heater delivery location.
2. Providing additional heated water tank storage capacity above peak SHW demand with equivalent peak storage capac- ity to Item 1.

Credits earned for measure G06 shall be calculated using Equation 4-33:

**Equation 4-33** *EC*G06\_*ach* = *EC*G06\_*base* × *EC*G06\_*adj*

where:

*EC*G06*\_ach* = SWH energy storage credit achieved for project.

*EC*G06*\_base* = G06 Base energy credit from Section C406.3.

*EC*G06*\_adj* = Energy credit adjustment factor from Table C406.3.7.

|  |  |  |  |
| --- | --- | --- | --- |
| **TABLE C406.3.7—ENERGY CREDIT ADJUSTMENT BASED ON USE OF HEAT PUMP WATER HEATER OR DEMAND RESPONSE** | | | |
| **DEMAND RESPONSE READY PER SECTION C404.10** | **DEMAND RESPONSE SIGNAL AVAILABLEa** | **HAS HPWH** | **b**  ***EC*GO6\_*adj*** |
| No | NA | No | 100% |
| No | NA | Yes | 33% |
| Yes | No | No | 50% |
| Yes | No | Yes | 17% |
| Yes | Yes | NA | 0% |
| HPWH = Heat Pump Water Heater, NA = Not available.   1. “Demand Response Signal Available” is “Yes” where a controlling entity currently makes a demand response signal available to the building. 2. The lower values of *EC*G06\_*adj* in this column apply where not less than 67 percent of the whole-building design end use service water heating requirements are met using only heat pump heating at the conditions described in Section C406.2.3.1.2. | | | |

**C406.3.8 G07 Building thermal mass.** The project shall have additional passive interior mass and a night flush control of the HVAC system. The credit is available to projects that have at least 80 percent of gross floor area unoccupied between midnight and 6:00 a.m. The project shall meet the following requirements:

* 1. Interior to the *building thermal envelope* insulation, provide 10 pounds per foot (15 kg/m) of project *conditioned floor area* of passive thermal mass in the *building* interior wall, the inside of the *exterior wall* or the interior floor construction. Mass construction shall have mass surfaces directly contacting the air in *conditioned spaces* with directly attached gypsum panels allowed. Mass with carpet or furred gypsum panels or exterior wall mass that is on the exterior of the insulation layer [e.g., the portion of concrete masonry unit (CMU) block on the exterior of insulation-filled cell cavities] shall not be included toward the building mass required.
  2. HVAC units for 80 percent or more of the supply airflow in the project shall be equipped with outdoor air economizers and fans that have variable or low speed capable of operating at 66 percent or lower airflow and be included in the night flush control sequence.
  3. Night flush controls shall be configured with the following sequence or another night flush strategy shall be permitted where demonstrated to be effective, avoids added morning heating and is *approved* by the authority having jurisdiction.
     1. Summer mode shall be activated when outdoor air temperature exceeds 70°F (21°C) and shall continue unin- terrupted until deactivated when outdoor air temperature falls below 45°F (7°C). During summer mode, the occupied cooling setpoint shall be set 1°F (0.6°C) higher than normal and the occupied heating setpoint shall be reset 2°F (1.1°C) lower than normal.
     2. Where all the following conditions exist, night flush shall be activated:
        1. Summer mode is active in accordance with Item 3.1.
        2. Outdoor air temperature is 5°F (2.8°C) or more below indoor average *zone* temperature.
        3. Indoor average *zone* temperature is greater than morning occupied heating setpoint.
        4. In Climate Zones 0A, 1A, 2A and 3A, outdoor dewpoint is below 50°F (10°C) or outdoor air enthalpy is less than indoor air enthalpy.
        5. Local time is between 10:00 p.m. and 6:00 a.m.
     3. When night flush is active, *automatic* night flush controls shall operate outdoor air economizers at low fan speed not exceeding 66 percent during the unoccupied period with mechanical cooling and heating locked out.

SECTION C407—SIMULATED BUILDING PERFORMANCE

**C407.1 Scope.** This section establishes criteria for compliance using *simulated building performance*. The following systems and loads shall be included in determining the *simulated building performance*: heating systems, cooling systems, *service water heating*, *fan systems*, lighting power, receptacle loads and process loads.

**Exception:** Energy used to recharge or refuel vehicles that are used for on-road and off-site transportation purposes.

**C407.2 Mandatory requirements.** Compliance based on *simulated building performance* requires that a *proposed design* meet all of the following:

1. The requirements of the sections indiced within Table C407.2(1).
2. ~~An annual~~ *~~energy cost~~* A site energy usethat is less than or equal to the percentage of the ~~annual~~ *~~energy cost~~* ~~(PAEC)~~ site energy use (SEUC) of the *standard reference design* calculated in Equation 4-34. ~~Energy prices shall be taken from a source~~ *~~approved~~* ~~by the~~ *~~code official~~*~~, such as the Department of Energy, Energy Information Administration’s~~ *~~State Energy Data System Prices and Expenditures~~* ~~reports.~~ *~~Code officials~~* ~~shall be permitted to require time-of-use pricing in~~ *~~energy cost~~* ~~calculations.~~ The reduction in *~~energy cost~~* site energy use of the *proposed design* associated with *on-site and off-site renewable energy* shall ~~be~~ not ~~more than 5 percent of the total~~ *~~energy cost~~* be included in the total site energy use. ~~The amount of renewable energy purchased from off-site sources shall be the same in the~~ *~~standard reference design~~* ~~and the~~ *~~proposed design~~*~~.~~

**Equation 4-34** *~~PAEC~~ PSEUC*= 100 × (0.80 + 0.025 - *ECr*/1,000)

where:

~~PAEC~~ *PSEUC* = The percentage of the ~~annual energy cost~~ site energy use of the standard reference design.

*ECr* = Energy efficiency credits required for the building in accordance with Section C406.1 (do not include load manage- ment and renewable credits).

Exceptions:

* 1. Jurisdictions that require site energy (1 kWh = 3413 Btu) rather than *energy cost* as the metric of comparison.
  2. Where energy use based on source energy expressed in Btu or Btu per square foot of *conditioned floor area* is substituted for the *energy cost*, the energy use shall be calculated using source energy factors from Table C407.2(2). For electricity, US locations shall use values from eGRID subregions. Locations outside the United States shall use the value for “All other electricity” or locally derived values.

|  |  |
| --- | --- |
| **TABLE C407.2(1)—REQUIREMENTS FOR SIMULATED BUILDING PERFORMANCE** | |
| **SECTIONa** | **TITLE** |
| **Envelope** | |
| C401.3 | Building thermal envelope certificate |
| C402.2.1.1 | Joints staggered |
| C402.2.1.2 | Skylight curbs |
| C402.2.6 | Insulation of radiant heating system panels |
| C402.5.1.3 | Fenestration orientation |
| C402.6 | Air leakage—building thermal envelope |
| **Mechanical** | |
| C403.1.1 | Calculation of heating and cooling loads |
| C403.1.2 | Data centers |
| C403.2 | System design |
| C403.3 | Heating and cooling equipment efficiencies |
| C403.4.1 | Thermostatic controls |
| C403.4.2 | Off-hour controls |
| C403.4.7 | Heating and cooling system controls for operable openings to the outdoors |
| C403.5.5 | Economizer fault detection and diagnostics |
| C403.7, except C403.7.4.1 | Ventilation and exhaust systems |
| C403.8, except C403.8.6 | Fan and fan controls |
| C403.9 | Large-diameter ceiling fans |
| C403.12, except C403.12.3 | Refrigeration equipment performance |
| C403.13 | Construction of HVAC system elements |
| C403.14 | Mechanical systems located outside of the building thermal envelope |
| C404 | Service water heating |
| C405, except C405.3 | Electrical power and lighting systems |
| C406.1.2 | Additional renewable and load management credit requirements |
| C408 | Maintenance information and system commissioning |
| a. Reference to a code section includes all the relative subsections except as indicated in the table. | |

|  |  |
| --- | --- |
| **TABLE C407.2(2)—SOURCE ENERGY CONVERSION FACTORS FOR ELECTRICITY** | |
| **SOURCE ENERGY** | **CONVERSION FACTOR** |
| **Fossil Fuels Delivered to Buildings** | |
| Natural gas | 1.092 |
| LPG or propone | 1.151 |
| Fuel oil (residual) | 1.191 |
| Fuel oil (distillate) | 1.158 |
| Coal | 1.048 |
| Gasoline | 1.187 |
| Other fuels not specified in this table | 1.048 |
| **Electricity** | |
| AKGD-ASCC Alaska Grid | 2.47 |
| AKMS-ASCC Miscellaneous | 1.35 |
| AZNM-WECC Southwest | 2.57 |
| CAMX-WECC California | 1.66 |
| ERCT-ERCOT All | 2.32 |
| FRCC-FRCC All | 2.78 |

|  |  |
| --- | --- |
| **TABLE C407.2(2)—SOURCE ENERGY CONVERSION FACTORS FOR ELECTRICITY—continued** | |
| **SOURCE ENERGY** | **CONVERSION FACTOR** |
| **Electricity—continued** | |
| HIMS-HICC Miscellaneous | 3.15 |
| HIOA-HICC Oahu | 3.87 |
| MROE-MRO East | 2.92 |
| MROW-MRO West | 2.21 |
| NEWE-NPCC New England | 2.66 |
| NWPP-WECC Northwest | 1.48 |
| NYCW-NPCC NYC/Westchester | 2.89 |
| NYLI-NPCC Long Island | 2.84 |
| NYUP-NPCC Upstate NY | 1.81 |
| PRMS-Puerto Rico Miscellaneous | 3.27 |
| RFCE-RFC East | 2.90 |
| RFCM-RFC Michigan | 2.93 |
| RFCW-RFC West | 2.97 |
| RMPA-WECC Rockies | 2.16 |
| SPNO-SPP North | 2.21 |
| SPSO-SPP South | 2.05 |
| SRMV-SERC Mississippi Valley | 2.84 |
| SRMW-SERC Midwest | 3.09 |
| SRSO-SERC South | 2.89 |
| SRTV-SERC Tennessee Valley | 2.82 |
| SRVC-SERC Virginia/Carolina | 2.91 |
| All other electricity | 2.51 |
| **Thermal Energy** | |
| Chilled water | 0.60 |
| Steam | 1.84 |
| Hot water | 1.73 |

**C407.3 Documentation.** Documentation verifying that the methods and accuracy of compliance software tools conform to the provisions of this section shall be provided to the *code official.*

**C407.3.1 Compliance report.** Permit submittals shall include a report documenting that the *proposed design* has annual energy costs less than or equal to the annual energy costs of the *standard reference design*. The compliance documentation shall include the following information:

1. Address of the *building*.
2. An inspection checklist documenting the building component characteristics of the *proposed design* as specified in Table C407.4.1(1). The inspection checklist shall show the estimated annual *energy cost* for both the *standard reference design* and the *proposed design*.
3. Name of individual completing the compliance report.
4. Name and version of the compliance software tool.

**C407.3.2 Additional documentation.** The *code official* shall be permitted to require the following documents:

1. Documentation of the building component characteristics of the *standard reference design*.
2. Thermal zoning diagrams consisting of floor plans showing the thermal zoning scheme for *standard reference design* and

*proposed design*.

1. Input and output reports from the *energy analysis* simulation program containing the complete input and output files, as applicable. The output file shall include energy use totals and energy use by energy source and end-use served, total hours that space conditioning loads are not met and any errors or warning messages generated by the simulation tool as applicable.
2. An explanation of any error or warning messages appearing in the simulation tool output.
3. A certification signed by the builder providing the building component characteristics of the *proposed design* as given in Table C407.4.1(1).
4. Documentation of the reduction in energy use associated with *on-site renewable energy*.

**C407.4 Calculation procedure.** Except as specified by this section, the *standard reference design* and *proposed design* shall be configured and analyzed using identical methods and techniques.

**C407.4.1 Building specifications.** The *standard reference design* and *proposed design* shall be configured and analyzed as speci- fied by Table C407.4.1(1). Table C407.4.1(1) shall include by reference all notes contained in Table C402.1.2.

|  |  |  |
| --- | --- | --- |
| **TABLE C407.4.1(1)—SPECIFICATIONS FOR THE STANDARD REFERENCE AND PROPOSED DESIGNS** | | |
| **BUILDING COMPONENT CHARACTERISTICS** | **STANDARD REFERENCE DESIGN** | **PROPOSED DESIGN** |
| Space use classification | Same as proposed | The space use classification shall be chosen in accor- dance with Table C405.3.2(1) or C405.3.2(2) for all areas of the building covered by this permit. Where the space use classification for a building is not known, the building shall be categorized as an office building. |
| Roofs | Type: insulation entirely above deck | As proposed |
| Gross area: same as proposed | As proposed |
| *U*-factor: as specified in Table C402.1.2 | As proposed |
| Solar reflectance: 0.25, except as specified in Section C402.4 and Table C402.4 for Climate Zones 0, 1, 2 and 3 | As proposed |
| Emittance: 0.90, except as specified in Section C402.4 and Table C402.4 for Climate Zones 0, 1, 2 and 3 | As proposed |
| Walls, above-grade | Type: same as proposed | As proposed |
| Gross area: same as proposed | As proposed |
| *U*-factor: as specified in Table C402.1.2 | As proposed |
| Thermal bridges: account for heat transfer consistent with compliant psi- and chi-factors from Table C402.1.4 for ther- mal bridges as identified in Section C402.7 that are present in the proposed design | As proposed; psi- and chi-factors for proposed thermal bridges shall be determined in accordance with requirements in Section C402.1.4. |
| Solar reflectance: 0.25 | As proposed |
| Emittance: 0.90 | As proposed |
| Walls, below-grade | Type: mass wall | As proposed |
| Gross area: same as proposed | As proposed |
| *U*-factor: as specified in Table C402.1.2 with insulation layer on interior side of walls | As proposed |
| Floors, above-grade | Type: joist/framed floor | As proposed |
| Gross area: same as proposed | As proposed |
| *U*-factor: as specified in Table C402.1.2 | As proposed |
| Floors, slab-on-grade | Type: unheated | As proposed |
| *F*-factor: as specified in Table C402.1.2 | As proposed |
| Opaque doors | Type: swinging | As proposed |
| Area: Same as proposed | As proposed |
| *U*-factor: as specified in Table C402.1.2 | As proposed |

|  |  |  |
| --- | --- | --- |
| **TABLE C407.4.1(1)—SPECIFICATIONS FOR THE STANDARD REFERENCE AND PROPOSED DESIGNS—continued** | | |
| **BUILDING COMPONENT CHARACTERISTICS** | **STANDARD REFERENCE DESIGN** | **PROPOSED DESIGN** |
| Vertical fenestration other than opaque doors | Area   1. The proposed vertical fenestration area; where the proposed vertical fenestration area is less than 40 percent of above-grade wall area. 2. Forty percent of above-grade wall area; where the proposed vertical fenestration area is 40 percent or more of the above-grade wall area. 3. Fenestration orientation shall comply with Section   C402.5.1.3. | As proposed |
| *U*-factor: as specified in Table C402.5 | As proposed |
| 1. SHGC: as specified in Table C402.5 except that for climates with no requirement (NR), SHGC = 0.40 shall be used 2. Fenestration SHGC shall comply with Section   C402.5.1.3. | As proposed |
| External shading and PF: none | As proposed |
| Skylights | Area   1. The proposed skylight area; where the proposed skylight area is less than that permitted by Section C402.1. 2. The area permitted by Section C402.1; where the proposed skylight area exceeds that permitted by Section C402.1. | As proposed |
| *U*-factor: as specified in Table C402.5 | As proposed |
| SHGC: as specified in Table C402.5 except that for climates with no requirement (NR), SHGC = 0.40 shall be used | As proposed |
| Lighting, interior | The interior lighting power shall be determined in accor- dance with Section C405.3.2. Where the occupancy of the building is not known, the lighting power density shall be  1.0 watt per square foot based on the categorization of buildings with unknown space classification as offices. | As proposed |
| Lighting, exterior | The lighting power shall be determined in accordance with Tables C405.5.2(1), C405.5.2(2) and C405.5.2(3). Areas and  dimensions of surfaces shall be the same as proposed. | As proposed |
| Internal gains | Same as proposed | Receptacle, motor and process loads shall be modeled and estimated based on the space use classification. End-use load components within and associated with the building shall be modeled to include, but not be limited to, the following: exhaust fans, parking garage ventilation fans, exterior building lighting, swimming pool heaters and pumps, elevators, escalators, refrig- eration equipment and cooking equipment. |
| Schedules | Same as proposed  **Exception:** Thermostat settings and schedules for HVAC systems that utilize radiant heating, radiant cooling and elevated air speed, provided that equivalent levels of occupant thermal comfort are demonstrated by means of equal Standard Effective Temperature as calculated in Normative Appendix B of ASHRAE Standard 55. | Operating schedules shall include hourly profiles for daily operation and shall account for variations between weekdays, weekends, holidays and any seasonal operation. Schedules shall model the time- dependent variations in occupancy, illumination, receptacle loads, thermostat settings, mechanical ventilation, HVAC equipment availability, service hot water usage and any process loads. The schedules shall be typical of the proposed building type as deter- mined by the designer and approved by the jurisdiction. |
| Outdoor airflow | Where the proposed design specifies mechanical ventilation:   1. For systems 1–4 as specified in Tables C407.4.1(2) and C407.4.1(3), the outdoor airflow rate shall be determined in accordance with Section C403.7 and Section 403.3.1.1.2.3.4, Equation 4-8, of the *International Mechanical Code* using a system ventilation efficiency (*Ev*) of 0.75. 2. For systems 5–11 as specified in Tables C407.4.1(2) and C407.4.1(3), the outdoor airflow rate shall be determined in accordance with Section C403.7 and Section 403.3 of the *International Mechanical Code*.   Where the proposed design specifies natural ventilation, as proposed. | As proposed, in accordance with Section C403.2.2. |

|  |  |  |
| --- | --- | --- |
| **TABLE C407.4.1(1)—SPECIFICATIONS FOR THE STANDARD REFERENCE AND PROPOSED DESIGNS—continued** | | |
| **BUILDING COMPONENT CHARACTERISTICS** | **STANDARD REFERENCE DESIGN** | **PROPOSED DESIGN** |
| Heating systems | Fuel type: same as proposed design | As proposed |
| Equipment typea: as specified in Tables C407.4.1(2) and C407.4.1(3) | As proposed |
| Efficiency: as specified in the tables in Section C403.3.2. | As proposed |
| Capacityb: sized proportionally to the capacities in the proposed design based on sizing runs, and shall be estab- lished such that no smaller number of unmet heating load hours and no larger heating capacity safety factors are provided than in the proposed design. | As proposed |
| Cooling systems | Fuel type: same as proposed design | As proposed |
| Equipment typec: as specified in Tables C407.4.1(2) and C407.4.1(3) | As proposed |
| Efficiency: as specified in Tables C403.3.2(1), C403.3.2(2) and C403.3.2(3) | As proposed |
| Capacityb: sized proportionally to the capacities in the proposed design based on sizing runs, and shall be estab- lished such that no smaller number of unmet cooling load hours and no larger cooling capacity safety factors are provided than in the proposed design. | As proposed |
| Economizerd: same as proposed, in accordance with Section C403.5. | As proposed |
| Service water heatinge | Fuel type: same as proposed | As proposed |
| Efficiency: as specified in Table C404.2 | For Group R, as proposed multiplied by SWHF.  For other than Group R, as proposed multiplied by efficiency as provided by the manufacturer of the DWHR unit. |
| Capacity: same as proposed | As proposed |
| Where no service water hot water system exists or is speci- fied in the proposed design, no service hot water heating shall be modeled. |
| Energy recovery | Where the proposed design specifies mechanical ventila- tion, as specified in Section C403.7.4 based on the standard reference design airflows. | As proposed |
| Where the proposed design specifies natural ventilation, as proposed. |
| Fan power | As specified in Section C403.8 for the proposed design.  **Exceptions:**   1. Where the fan power of the proposed design is exempted from the requirements of Section C403.8, as proposed. 2. Fan systems addressed by Section C403.8.1: fan system BHP shall be as proposed or to the limits specified in Section C403.8.1, whichever is smaller. If the limit is reached, the power of each fan shall be reduced proportionally until the limit is met. 3. Fan systems serving areas where the mechanical ventilation is provided in accordance with an engineered ventilation system design of Section   403.2 of the *International Mechanical Code* shall not use the particulate filtration or air cleaner pressure drop adjustment available in Table C403.8.1(1) when calculating the fan system BHP limit for the portion of the airflow being treated to comply with the engineered ventilation system design. | As proposed |

|  |  |  |
| --- | --- | --- |
| **TABLE C407.4.1(1)—SPECIFICATIONS FOR THE STANDARD REFERENCE AND PROPOSED DESIGNS—continued** | | |
| **BUILDING COMPONENT CHARACTERISTICS** | **STANDARD REFERENCE DESIGN** | **PROPOSED DESIGN** |
| On-site renewable energy | Where a system providing on-site renewable energy has been modeled in the proposed design, the same system shall be modeled identically in the standard reference design except the rated capacity shall meet the require- ments of Section C405.15.1  Where no system is designed or included in the proposed design, model an unshaded photovoltaic system with the following characteristics:  Size: rated capacity per Section C405.15.1.  Module type: crystalline silicone panel with glass cover, 19.1% nominal efficiency and temperature coefficient of  -0.35%/°C. Performance shall be based on a reference temperature of 77°F (25°C), air mass of 1.5 atmosphere and irradiance of 317 Btu/h × ft2 (1000 W/m2).  Array type: rack-mounted array with installed nominal operating cell temperature (INOCT) of 103°F (45°C).  Total system losses (DC output to AC output): 11.3%. Tilt: 0 degrees (mounted horizontally).  Azimuth: 180 degrees. | As proposed |
| For SI: 1 watt per square foot = 10.7 w/m2.  SWHF = Service Water Heat Recovery factor, DWHR = Drain Water Heat Recovery.   1. Where no heating system exists or has been specified, the heating system shall be modeled as fossil fuel. The system characteristics shall be identical in both the standard reference design and proposed design. 2. The ratio between the capacities used in the annual simulations and the capacities determined by sizing runs shall be the same for both the standard reference design and proposed design. 3. Where no cooling system exists or no cooling system has been specified, the cooling system shall be modeled as an air-cooled single-zone system, one unit per thermal zone. The system characteristics shall be identical in both the standard reference design and proposed design. 4. If an economizer is required in accordance with Table C403.5(1) and where no economizer exists or is specified in the proposed design, then a supply-air economizer shall be provided in the standard reference design in accordance with Section C403.5. 5. The SWHF shall be applied as follows:    1. Where potable water from the DWHR unit supplies not less than one shower and not greater than two showers, of which the drain water from the same showers flows through the DWHR unit then SWHF = [1 **–** (DWHR unit efficiency × 0.36)].    2. Where potable water from the DWHR unit supplies not less than three showers and not greater than four showers, of which the drain water from the same showers flows through the DWHR unit then SWHF = [1 **–** (DWHR unit efficiency × 0.33)].    3. Where potable water from the DWHR unit supplies not less than five showers and not greater than six showers, of which the drain water from the same showers flows through the DWHR unit, then SWHF = [1 **–** (DWHR unit efficiency × 0.26)].    4. Where Items 1 through 3 are not met, SWHF = 1.0. | | |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **TABLE C407.4.1(2)—HVAC SYSTEMS MAP** | | | | |
| **CONDENSER COOLING SOURCEa** | **HEATING SYSTEM CLASSIFICATIONb** | **STANDARD REFERENCE DESIGN HVC SYSTEM TYPEc** | | |
| **Single-zone Residential System** | **Single-zone Nonresidential System** | **All Other** |
| Water/ground | Electric resistance | System 5 | System 5 | System 1 |
| Heat pump | System 6 | System 6 | System 6 |
| Fossil fuel | System 7 | System 7 | System 2 |
| Air/none | Electric resistance | System 8 | System 9 | System 3 |
| Heat pump | System 8 | System 9 | System 3 |
| Fossil fuel | System 10 | System 11 | System 4 |
| 1. Select “water/ground” where the proposed design system condenser is water or evaporatively cooled; select “air/none” where the condenser is air cooled. Closed-circuit dry coolers shall be considered to be air cooled. Systems utilizing district cooling shall be treated as if the condenser water type were “water.” Where mechanical cooling is not specified or the mechanical cooling system in the proposed design does not require heat rejection, the system shall be treated as if the condenser water type were “Air.” For proposed designs with ground-source or groundwater-source heat pumps, the standard reference design HVAC system shall be water-source heat pump (System 6). 2. Select the path that corresponds to the proposed design heat source: electric resistance, heat pump (including air source and water source), or fuel fired. Systems utilizing district heating (steam or hot water) and systems without heating capability shall be treated as if the heating system type were “fossil fuel.” For systems with mixed fuel heat- ing sources, the system or systems that use the secondary heating source type (the one with the smallest total installed output capacity for the spaces served by the system) shall be modeled identically in the standard reference design and the primary heating source type shall be used to determine standard reference design HVAC system type. 3. Select the standard reference design HVAC system category: The system under “single-zone residential system” shall be selected where the HVAC system in the proposed design is a single-zone system and serves a Group R occupancy. The system under “single-zone nonresidential system” shall be selected where the HVAC system in the proposed design is a single-zone system and serves other than Group R occupancy. The system under “all other” shall be selected for all other cases. | | | | |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **TABLE C407.4.1(3)—SPECIFICATIONS FOR THE STANDARD REFERENCE DESIGN HVAC SYSTEM DESCRIPTIONS** | | | | |
| **SYSTEM NO.** | **SYSTEM TYPE** | **FAN CONTROL** | **COOLING TYPE** | **HEATING TYPE** |
| 1 | Variable air volume with parallel fan- powered boxesa | VAVd | Chilled watere | Electric resistance |
| 2 | Variable air volume with reheatb | VAVd | Chilled watere | Hot water fossil fuel boilerf |
| 3 | Packaged variable air volume with parallel fan-powered boxesa | VAVd | Direct expansionc | Electric resistance |
| 4 | Packaged variable air volume with reheatb | VAVd | Direct expansionc | Hot water fossil fuel boilerf |
| 5 | Two-pipe fan coil | Constant volumei | Chilled watere | Electric resistance |
| 6 | Water-source heat pump | Constant volumei | Direct expansionc | Electric heat pump and boilerg |
| 7 | Four-pipe fan coil | Constant volumei | Chilled watere | Hot water fossil fuel boilerf |
| 8 | Packaged terminal heat pump | Constant volumei | Direct expansionc | Electric heat pumph |
| 9 | Packaged rooftop heat pump | Constant volumei | Direct expansionc | Electric heat pumph |
| 10 | Packaged terminal air conditioner | Constant volumei | Direct expansion | Hot water fossil fuel boilerf |
| 11 | Packaged rooftop air conditioner | Constant volumei | Direct expansion | Fossil fuel furnace |
| For SI: 1 foot = 304.8 mm, 1 cfm = 0.4719 L/s, 1 Btu/h = 0.293/W, °C = [(°F) – 32]/1.8.   1. **VAV with parallel boxes:** Fans in parallel VAV fan-powered boxes shall be sized for 50 percent of the peak design flow rate and shall be modeled with 0.35 W/cfm fan power. Minimum volume setpoints for fan-powered boxes shall be equal to the minimum rate for the space required for ventilation consistent with Section C403.6.1, Item 3. Supply air temperature setpoint shall be constant at the design condition. 2. **VAV with reheat:** Minimum volume setpoints for VAV reheat boxes shall be 0.4 cfm/ft2 of floor area. Supply air temperature shall be reset based on zone demand from the design temperature difference to a 10°F temperature difference under minimum load conditions. Design airflow rates shall be sized for the reset supply air temperature (i.e., a 10°F temperature difference). 3. **Direct expansion:** The fuel type for the cooling system shall match that of the cooling system in the proposed design. 4. **VAV:** Where the proposed design system has a supply, return or relief fan motor 25 hp or larger, the corresponding fan in the VAV system of the standard reference design shall be modeled assuming a variable-speed drive. For smaller fans, a forward-curved centrifugal fan with inlet vanes shall be modeled. Where the proposed design’s system has a direct digital control system at the zone level, static pressure setpoint reset based on zone requirements in accordance with Section C403.8.6 shall be modeled. 5. **Chilled water:** For systems using purchased chilled water, the chillers are not explicitly modeled and chilled water costs shall be based as determined in Sections C407.2 and C407.4.2. Otherwise, the standard reference design’s chiller plant shall be modeled with chillers having the number as indicated in Table C407.4.1(4) as a function of standard reference building chiller plant load and type as indicated in Table C407.4.1(5) as a function of individual chiller load. Where chiller fuel source is mixed, the system in the standard reference design shall have chillers with the same fuel types and with capacities having the same proportional capacity as the proposed design’s chillers for each fuel type. Chilled water supply temperature shall be modeled at 44°F design supply temperature and 56°F return temperature. Piping losses shall not be modeled in either building model. Chilled water supply water temperature shall be reset in accordance with Section C403.4.4. Pump system power for each pumping system shall be the same as the proposed design; where the proposed design has no chilled water pumps, the standard reference design pump power shall be 22 W/gpm (equal to a pump oper- ating against a 75-foot head, 65 percent combined impeller and motor efficiency). The chilled water system shall be modeled as primary-only variable flow with flow maintained at the design rate through each chiller using a bypass. Chilled water pumps shall be modeled as riding the pump curve or with variable-speed drives where required in Section C403.4.4. The heat rejection device shall be an axial fan cooling tower with two-speed fans where required in Section C403.11. Condenser water design supply temperature shall be 85°F or 10°F approach to design wet-bulb temperature, whichever is lower, with a design temperature rise of 10°F. The tower shall be controlled to maintain a 70°F leaving water temperature where weather permits, floating up to leaving water temperature at design conditions. Pump system power for each pumping system shall be the same as the proposed design; where the proposed design has no condenser water pumps, the standard reference design pump power shall be 19 W/gpm (equal to a pump operating against a 60-foot head, 60 percent combined impeller and motor efficiency). Each chiller shall be modeled with separate condenser water and chilled water pumps interlocked to operate with the associated chiller. 6. **Fossil fuel boiler:** For systems using purchased hot water or steam, the boilers are not explicitly modeled and hot water or steam costs shall be based on actual utility rates. Otherwise, the boiler plant shall use the same fuel as the proposed design and shall be natural draft. The standard reference design boiler plant shall be modeled with a single boiler where the standard reference design plant load is 600,000 Btu/h and less and with two equally sized boilers for plant capacities exceeding 600,000 Btu/h. Boil- ers shall be staged as required by the load. Hot water supply temperature shall be modeled at 180°F design supply temperature and 130°F return temperature. Piping losses shall not be modeled in either building model. Hot water supply water temperature shall be reset in accordance with Section C403.4.4. Pump system power for each pump- ing system shall be the same as the proposed design; where the proposed design has no hot water pumps, the standard reference design pump power shall be 19 W/gpm (equal to a pump operating against a 60-foot head, 60 percent combined impeller and motor efficiency). The hot water system shall be modeled as primary only with contin- uous variable flow. Hot water pumps shall be modeled as riding the pump curve or with variable speed drives where required by Section C403.4.4. 7. **Electric heat pump and boiler:** Water-source heat pumps shall be connected to a common heat pump water loop controlled to maintain temperatures between 60°F and 90°F. Heat rejection from the loop shall be provided by an axial fan closed-circuit evaporative fluid cooler with two-speed fans where required in Section C403.8.6. Heat addi- tion to the loop shall be provided by a boiler that uses the same fuel as the proposed design and shall be natural draft. Where no boilers exist in the proposed design, the standard reference building boilers shall be fossil fuel. The standard reference design boiler plant shall be modeled with a single boiler where the standard reference design plant load is 600,000 Btu/h or less and with two equally sized boilers for plant capacities exceeding 600,000 Btu/h. Boilers shall be staged as required by the load. Piping losses shall not be modeled in either building model. Pump system power shall be the same as the proposed design; where the proposed design has no pumps, the standard reference design pump power shall be 22 W/gpm, which is equal to a pump operating against a 75-foot head, with a 65 percent combined impeller and motor efficiency. Loop flow shall be variable with flow shutoff at each heat pump when its compressor cycles off as required by Section C403.4.4. Loop pumps shall be modeled as riding the pump curve or with variable speed drives where required by Section C403.11. 8. **Electric heat pump:** Electric air-source heat pumps shall be modeled with electric auxiliary heat. The system shall be controlled with a multistage space thermostat and an outdoor air thermostat wired to energize auxiliary heat only on the last thermostat stage and when outdoor air temperature is less than 40°F. 9. **Constant volume:** Fans shall be controlled in the same manner as in the proposed design (i.e., fan operation whenever the space is occupied or fan operation cycled on calls for heating and cooling). Where the fan is modeled as cycling and the fan energy is included in the energy efficiency rating of the equipment, fan energy shall not be modeled explicitly. | | | | |

|  |  |
| --- | --- |
| **TABLE C407.4.1(4)—NUMBER OF CHILLERS** | |
| **TOTAL CHILLER PLANT CAPACITY** | **NUMBER OF CHILLERS** |
| ≤ 300 tons | 1 |
| > 300 tons, < 600 tons | 2, sized equally |
| ≥ 600 tons | 2 minimum, with chillers added so that all are sized equally and none is larger than 800 tons |
| For SI: 1 ton = 3517 W. | |

|  |  |  |
| --- | --- | --- |
| **TABLE C407.4.1(5)—WATER CHILLER TYPES** | | |
| **INDIVIDUAL CHILLER PLANT CAPACITY** | **ELECTRIC CHILLER TYPE** | **FOSSIL FUEL CHILLER TYPE** |
| ≤ 100 tons | Reciprocating | Single-effect absorption, direct fired |
| > 100 tons, < 300 tons | Screw | Double-effect absorption, direct fired |
| ≥ 300 tons | Centrifugal | Double-effect absorption, direct fired |
| For SI: 1 ton = 3517 W. | | |

**C407.4.2 Thermal blocks.** The *standard reference design* and *proposed design* shall be analyzed using identical *thermal blocks* as specified in Section C407.4.2.1, C407.4.2.2 or C407.4.2.3.

**C407.4.2.1 HVAC zones designed.** Where HVAC *zones* are defined on HVAC design drawings, each HVAC *zone* shall be modeled as a separate *thermal block*.

**Exception:** Different HVAC *zones* shall be allowed to be combined to create a single *thermal block* or identical *thermal blocks*

to which multipliers are applied, provided that:

1. The space use classification is the same throughout the *thermal block*.
2. All HVAC *zones* in the *thermal block* that are adjacent to glazed exterior walls face the same orientation or their orientations are within 45 degrees (0.79 rad) of each other.
3. All of the *zones* are served by the same HVAC system or by the same kind of HVAC system.

**C407.4.2.2 HVAC zones not designed.** Where HVAC *zones* have not yet been designed, *thermal blocks* shall be defined based on similar internal load densities, occupancy, lighting, thermal and temperature schedules, and in combination with the following guidelines:

1. Separate *thermal blocks* shall be assumed for interior and perimeter spaces. Interior spaces shall be those located more than 15 feet (4572 mm) from an *exterior wall*. Perimeter spaces shall be those located closer than 15 feet (4572 mm) from an *exterior wall*.
2. Separate *thermal blocks* shall be assumed for spaces adjacent to glazed *exterior walls*: a separate *zone* shall be provided for each orientation, except orientations that differ by not more than 45 degrees (0.79 rad) shall be permit- ted to be considered to be the same orientation. Each *zone* shall include floor area that is 15 feet (4572 mm) or less from a glazed perimeter wall, except that floor area within 15 feet (4572 mm) of glazed perimeter walls having more than one orientation shall be divided proportionately between *zones*.
3. Separate *thermal blocks* shall be assumed for spaces having floors that are in contact with the ground or exposed to ambient conditions from *zones* that do not share these features.
4. Separate *thermal blocks* shall be assumed for spaces having exterior ceiling or *roof assemblies* from *zones* that do not share these features.

**C407.4.2.3 Group R-2 occupancy buildings.** Group R-2 occupancy spaces shall be modeled using one *thermal block* per space except that those facing the same orientations are permitted to be combined into one *thermal block*. Corner units and units with roof or floor loads shall only be combined with units sharing these features.

**C407.5 Calculation software tools.** Calculation procedures used to comply with Section C407 shall apply an *approved* version of a performance analysis software tool capable of calculating the annual energy consumption of all building elements that differ between the *standard reference design* and the *proposed design*. The same *approved* version of the performance analysis tool shall be used to calculate the *proposed design* and *standard reference design*.

**C407.5.1 Software tool approval.** Any version of a performance analysis tool meeting the requirements of Sections C407.5.1.1 and C407.5.1.2 shall be permitted to be *approved.* Tools are permitted to be *approved* based on meeting a specified threshold for a jurisdiction. The *code official* shall be permitted to approve tools for a specified application or limited scope.

**C407.5.1.1 Software tool capabilities.** *Approved* software tools shall include the following capabilities:

1. *Building* operation for a full calendar year (8,760 hours).
2. Climate data for a full calendar year (8,760 hours) and shall reflect *approved* coincident hourly data for temperature, solar radiation, humidity and wind speed for the *building* location.
3. Ten or more thermal zones.
4. Thermal mass effects.
5. Hourly variations in occupancy, illumination, receptacle loads, *thermostat* settings, mechanical ventilation, HVAC equipment availability, service hot water usage and any process loads.
6. Part-load performance curves for mechanical equipment.
7. Capacity and efficiency correction curves for mechanical heating and cooling equipment.
8. Printed *code official* inspection checklist listing each of the *proposed design* component characteristics from Table C407.4.1(1) determined by the analysis to provide compliance, along with their respective performance ratings, including but not limited to *R-*value, *U-factor*, SHGC, HSPF, AFUE, SEER and EF.

**C407.5.1.2 Testing required by software vendors.** Prior to approval, software tools shall be tested by the software vendor in accordance with ASHRAE Standard 140, except Sections 7 and 8. During testing, hidden inputs that are not normally available to the user shall be permitted to avoid introducing source code changes strictly used for testing. Software vendors shall publish, on a publicly available website, the following ASHRAE Standard 140 test results, input files and modeler reports for each tested version of a software tool:

1. Test results that demonstrate the software tool was tested in accordance with ASHRAE Standard 140 and that meet or exceed the values for “The Minimum Number of Range Cases within the Test Group to Pass” for all test groups in ASHRAE Standard 140, Table A3-14.
2. Test results of the performance analysis tool and input files used for generating the ASHRAE Standard 140 test cases along with the results of the other performance analysis tools included in ASHRAE Standard 140, Annexes B8 and B16.
3. The modeler report in ASHRAE Standard 140, Annex A2, Attachment A2.7, Report Blocks A and G shall be completed for results exceeding the maximum or falling below the minimum of the reference values shown in ASHRAE Standard 140, Tables A3-1 through A3-13, and Report Blocks A and E shall be completed for any omitted results.

**C407.5.2 Algorithms not tested.** Algorithms not tested in accordance with Section C407.5.1.2, including algorithms that are alternatives to those that were tested, and numerical settings not tested, such as time steps and tolerances, shall be permitted to be used where modeling the *proposed design* and *standard reference design*.

**C407.5.3 Input values.** Where calculations require input values not specified by Sections C402, C403, C404 and C405, those input values shall be taken from an *approved* source.

**C407.5.4 Exceptional calculation methods.** Where the simulation program does not model a design, material or device of the *proposed design*, an exceptional calculation method shall be used where *approved* by the *code official*. Where there are multiple designs, materials or devices that the simulation program does not model, each shall be calculated separately and exceptional savings determined for each. The total exceptional savings shall not constitute more than half of the difference between the base- line *simulated building performance* and the proposed *simulated building performance*. Applications for approval of an exceptional method shall include all of the following:

1. Step-by-step documentation of the exceptional calculation method performed, detailed enough to reproduce the results.
2. Copies of all spreadsheets used to perform the calculations.
3. A sensitivity analysis of energy consumption where each of the input parameters is varied from half to double the value assumed.
4. The calculations shall be performed on a time step basis consistent with the simulation program used.
5. The performance rating calculated with and without the exceptional calculation method.

SECTION C408 —MAINTENANCE INFORMATION AND SYSTEM COMMISSIONING

**C408.1 General.** This section covers the provision of maintenance information and the commissioning of, and the functional testing requirements for, *building* systems.

**C408.1.1 Building operations and maintenance information.** The *building* operations and maintenance documents shall be provided to the *owner* and shall consist of manufacturers’ information, specifications and recommendations; programming procedures and data points; narratives; and other means of illustrating to the *owner* how the *building*, equipment and systems are intended to be installed, maintained and operated. Required regular maintenance actions for equipment and systems shall be clearly stated on a readily visible label. The label shall include the title or publication number for the operation and maintenance manual for that particular model and type of product.

**C408.2 Mechanical systems and service water-heating systems commissioning and completion require- ments.** Prior to the final mechanical and plumbing inspections, the *registered design professional or approved agency* shall provide evidence of mechanical systems *commissioning* and completion in accordance with the provisions of this section.

*Construction document* notes shall clearly indicate provisions for *commissioning* and completion requirements in accordance with this section and are permitted to refer to specifications for further requirements. Copies of all documentation shall be given to the *owner* or owner’s authorized agent and made available to the *code official* upon request in accordance with Sections C408.2.4 and C408.2.5.

**Exceptions:** The following systems are exempt:

1. *Buildings* with less than 10,000 square feet (929 m2) gross *conditioned floor area* and combined heating, cooling and service water heating capacity of less than 960,000 Btu/h (281 kW).
2. Components within *dwelling units* and *sleeping units* served by one of the following systems:
   1. Simple unitary or packaged HVAC equipment listed in Table C403.3.2(1), C403.3.2(2), C403.3.2(4) or C403.3.2(5), each serving one *zone* and controlled by a single *thermostat* in the *zone* served.
   2. Two-pipe heating systems installed in the dwelling, serving one or more *zones*.

**C408.2.1 Commissioning plan.** A *commissioning plan* shall be developed by a *registered design professional* or *approved agency*

and shall include the following items:

1. A narrative description of the activities that will be accomplished during each phase of *commissioning,* including the personnel intended to accomplish each of the activities.
2. A listing of the specific equipment, appliances or systems to be tested and a description of the tests to be performed.
3. Functions to be tested including, but not limited to, calibrations and economizer controls.
4. Conditions under which the test will be performed. Testing shall affirm winter and summer design conditions and full outside air conditions.
5. Measurable criteria for performance.

**C408.2.2 Systems adjusting and balancing.** HVAC systems shall be balanced in accordance with generally accepted engineering standards. Air and water flow rates shall be measured and adjusted to deliver final flow rates within the tolerances provided in the product specifications. Test and balance activities shall include air system and hydronic system balancing.

**C408.2.2.1 Air systems balancing.** Each supply air outlet and *zone* terminal device shall be equipped with means for air balancing in accordance with the requirements of Chapter 6 of the *International Mechanical Code*. Discharge dampers used for air-system balancing are prohibited on constant-volume fans and variable volume fans with motors 10 hp (18.6 kW) and larger. Air systems shall be balanced in a manner to first minimize throttling losses then, for fans with system power of greater than 1 hp (0.746 kW), fan speed shall be adjusted to meet design flow conditions.

**Exception:** Fans with fan motors of 1 hp (0.74 kW) or less are not required to be provided with a means for air balancing.

**C408.2.2.2 Hydronic systems balancing.** Individual hydronic heating and cooling coils shall be equipped with means for balancing and measuring flow. Hydronic systems shall be proportionately balanced in a manner to first minimize throttling losses, then the pump impeller shall be trimmed or pump speed shall be adjusted to meet design flow conditions. Each hydronic system shall have either the capability to measure pressure across the pump, or test ports at each side of each pump.

**Exception:** The following equipment is not required to be equipped with a means for balancing or measuring flow:

* 1. Pumps with pump motors of 5 hp (3.7 kW) or less.
  2. Where throttling results in not greater than 5 percent of the *nameplate horsepower* draw above that required if the impeller were trimmed.

**C408.2.3 Functional performance testing.** Functional performance testing specified in Sections C408.2.3.1 through C408.2.3.3 shall be conducted.

**C408.2.3.1 Equipment.** Equipment functional performance testing shall demonstrate the installation and operation of components, systems and system-to-system interfacing relationships in accordance with *approved* plans and specifications such that operation, function and maintenance serviceability for each of the commissioned systems are confirmed. Testing shall include all modes and *sequence of operation*, including under full-load, part-load and the following emergency conditions:

1. All modes as described in the *sequence* of *operation*.
2. Redundant or *automatic* back-up mode.
3. Performance of alarms.
4. Mode of operation upon a loss of power and restoration of power.

**Exception:** Unitary or packaged HVAC equipment listed in the tables in Section C403.3.2 that do not require supply air economizers.


**C408.2.3.2 Controls.** HVAC and service water-heating control systems shall be tested to document that control devices, components, equipment and systems are calibrated and adjusted and operate in accordance with *approved* plans and specifi- cations. Sequences of operation shall be functionally tested to document they operate in accordance with *approved* plans and specifications.

**C408.2.3.3 Economizers.** Air economizers shall undergo a functional test to determine that they operate in accordance with manufacturer’s specifications.

**C408.2.4 Preliminary commissioning report.** A preliminary report of *commissioning* test procedures and results shall be completed and certified by the *registered design professional* or *approved agency* and provided to the *building owner* or owner’s authorized agent. The report shall be organized with mechanical and service hot water findings in separate sections to allow inde- pendent review. The report shall be identified as “Preliminary Commissioning Report,” shall include the completed Commissioning Compliance Checklist, Figure C408.2.4, and shall identify:

1. Itemization of deficiencies found during testing required by this section that have not been corrected at the time of report preparation.
2. Deferred tests that cannot be performed at the time of report preparation because of climatic conditions.
3. Climatic conditions required for performance of the deferred tests.
4. Results of functional performance tests.
5. Functional performance test procedures used during the commissioning process, including measurable criteria for test acceptance.

**FIGURE C408.2.4—COMMISSIONING COMPLIANCE CHECKLIST**



**C408.2.4.1 Acceptance of report.** *Buildings*, or portions thereof, shall not be considered as acceptable for a final inspection pursuant to Section C107.2.6 until the *code official* has received the Preliminary Commissioning Report from the *building owner* or owner’s authorized agent.

**C408.2.4.2 Copy of report.** The *code official* shall be permitted to require that a copy of the Preliminary Commissioning Report be made available for review by the *code official*.

**C408.2.5 Documentation requirements.** The *construction documents* shall specify that the documents described in this section be provided to the *building owner* or owner’s authorized agent within 90 days of the date of receipt of the *certificate of occupancy*.

**C408.2.5.1 System balancing report.** A written report describing the activities and measurements completed in accordance with Section C408.2.2.

**C408.2.5.2 Final commissioning report.** A report of test procedures and results identified as “Final Commissioning Report” shall be delivered to the *building owner* or owner’s authorized agent. The report shall be organized with mechanical system and service hot water system findings in separate sections to allow independent review. The report shall include the following:

* 1. Results of functional performance tests.
  2. Disposition of deficiencies found during testing, including details of corrective measures used or proposed.
  3. Functional performance test procedures used during the commissioning process including measurable criteria for test acceptance, provided herein for repeatability.

**Exception:** Deferred tests that cannot be performed at the time of report preparation due to climatic conditions.

**C408.3 Functional testing of lighting and receptacle controls.** *Automatic* lighting and receptacle controls required by this code shall comply with this section.

**C408.3.1 Functional testing.** Prior to passing final inspection, the *registered design professional* or *approved agency* shall provide evidence that the lighting and receptacle control systems have been tested to ensure that control hardware and software are cali- brated, adjusted, programmed and in proper working condition in accordance with the *construction documents* and manufacturer’s instructions. Functional testing shall be in accordance with Sections C408.3.1.1 through C408.3.1.3 for the appli- cable control type.

**C408.3.1.1 Occupant sensor controls.** Where *occupant sensor controls* are provided, the following procedures shall be performed:

1. Certify that the *occupant sensor* has been located and aimed in accordance with manufacturer recommendations.
2. For projects with seven or fewer *occupant sensors*, each sensor shall be tested.
3. For projects with more than seven *occupant sensors,* testing shall be done for each unique combination of sensor type and space geometry. Where multiples of each unique combination of sensor type and space geometry are provided, not less than 10 percent and in no case fewer than one, of each combination shall be tested unless the *code official* or design professional requires a higher percentage to be tested. Where 30 percent or more of the tested controls fail, all remaining identical combinations shall be tested.

For *occupant sensor controls* to be tested, verify the following:

* 1. Where *occupant sensor controls* include status indicators, verify correct operation.
  2. The lights and receptacles controlled by *occupant sensor controls* turn off or down to the permitted level within the required time upon vacancy of the space.
  3. For auto-on *occupant sensor controls*, the lights and receptacles controlled by *occupant sensor controls* turn on to the permitted level when an occupant enters the space.
  4. For manual-on *occupant sensor controls*, the lights and receptacles controlled by *occupant sensor controls*

turn on only when manually activated.

* 1. The lights are not incorrectly turned on by movement in adjacent areas or by HVAC operation.

**C408.3.1.2 Time-switch controls.** Where *time-switch controls* are provided, Items 1 through 5 shall be performed for all *time- switch controls*. For projects with more than seven spaces where lighting or receptacles are controlled by *time-switch controls*, not less than 10 percent of spaces and in no case fewer than one space shall be tested according to Items 6 and 7 unless the *code official* or *registered design professional* requires a higher percentage to be tested. Where 30 percent or more of the tested spaces fail any of the requirements in Items 6 and 7, all remaining spaces shall be tested.

1. Confirm that the *time-switch control* is programmed with accurate weekday, weekend and holiday schedules.
2. Provide documentation to the *owner* of *time-switch controls* programming including weekday, weekend, holiday schedules, and set-up and preference program settings.
3. Verify the correct time and date in the time switch.
4. Verify that any battery back-up is installed and energized.
5. Verify that the override time limit is set to not more than 2 hours.
6. Simulate occupied condition. Verify and document the following:
   1. All lights can be turned on and off by their respective area control switch.
   2. The switch only operates lighting in the *enclosed space* in which the switch is located.
   3. Receptacles in the space controlled by the *time-switch controls* turn on.
7. Simulate unoccupied condition. Verify and document the following:
   1. Nonexempt lighting turns off.
   2. *Manual* override switch allows only the lights and receptacles controlled by the time-switch controls in the *enclosed space* where the override switch is located to turn on controlled lighting and receptacles for more than 2 hours.
   3. Receptacles controlled by the *time-switch controls* turn off.
8. Additional testing as specified by the *registered design professional.*

**C408.3.1.3 Daylight responsive controls.** Where *daylight responsive controls* are provided, the following shall be verified:

1. Control devices have been properly located, field calibrated and set for accurate setpoints and threshold light levels.
2. Daylight controlled lighting loads adjust to light level setpoints in response to available daylight.
3. The calibration adjustment equipment is located for *ready access* only by authorized personnel.

**C408.3.1.4 High-end trim controls.** Where lighting controls are configured for *high-end trim*, verify the following:

1. *High-end trim* maximum level has been set.
2. The calibration adjustment equipment is located for *ready access* only by authorized personnel.
3. Lighting controls with *ready access* for users cannot increase the lighting power above the maximum level estab- lished by the *high-end trim* controls.

**C408.3.1.5 High-end trim lighting control verification for L02 Additional Efficiency Credit.** For the qualifying spaces asso- ciated with the project receiving the additional efficiency credits in Section C406.2.5.2, the following shall be documented while *daylight responsive controls* are not reducing lighting power:

1. The maximum setting for power or light output for each control group of general lighting luminaires.
2. The *high-end trim* setting for power or light output for each control group of general lighting luminaires.
3. For projects with seven or fewer claimed qualifying spaces, the reduction in light output or reduction in power due to *high-end trim* shall be tested in all spaces and shown to reduce the general lighting power or light output to not greater than 85 percent of full power or light output. For projects with more than seven claimed qualifying spaces, the reduction in light output or reduction in power due to *high-end trim* shall be tested in not less than 10 percent of spaces, and not less than seven spaces, and be shown to reduce general lighting power or light output to not greater than 85 percent of full power or light output. Where more than 30 percent of the tested spaces fail, the remaining qualifying spaces shall be tested.
4. Summarize the reduction in general lighting power or light output resulting from the *high-end trim* setting for each qualifying space and the floor area of each qualifying space.
5. Summarize the fraction of total floor area for spaces where *high-end trim* reduces general lighting power or light output to not greater than 85 percent of full power or light output.

**C408.3.1.6 Demand responsive lighting controls G01.** For spaces associated with the project receiving renewable and load management credits in Section C406.3.2, the following procedures shall be performed:

1. Confirm the maximum setpoint upon receipt of the *demand response signal* has been established for each space.
2. For projects with seven or fewer spaces with controls, each space shall be tested.
3. For projects with more than seven spaces with controls, testing shall be done for each unique space type. Where multiple spaces of each space type exist, not less than 10 percent of each space type, and in no case fewer than one space, shall be tested unless the *code official* requires a higher percentage to be tested. Where 30 percent or more of the tested controls fail in a space type, all remaining identical space types shall be tested.
4. For demand responsive controls to be tested, verify the following:
   1. Where *high-end trim* controls are used, the *high-end trim* shall be set before testing.
   2. Turn off all nongeneral lighting in the space.
   3. Set *general lighting* to its maximum illumination level. Where *high-end trim* is set, this will be the maximum illumination level at the *high-end trim* setpoint.
   4. An illumination measurement shall be taken in an area of the space not controlled by daylight responsive controlled lighting. If there is not an area without *daylight responsive controls*, the *daylight responsive controls* shall be overridden from reducing the lighting level during the test.
   5. Measure and document the maximum illumination level of the space.
5. Simulate a *demand response signal* and measure the illumination level at the same location as for the measurement in Section C408.3.1.6, Item 4.5. Verify the illumination level has been reduced to not greater than 80 percent of the maximum illumination level documented in Section C408.3.1.6, Item 4.5.
6. Simulate the end of a demand event by turning off the *demand response signal*; confirm controls automatically return to their normal operational settings at the end of the demand response event.

**C408.3.2 Documentation requirements.** The *construction documents* shall specify that the documents described in this section be provided to the *building owner* or owner’s authorized agent within 90 days of the date of receipt of the *certificate of occupancy*.

**C408.3.2.1 Drawings.** *Construction documents* shall include the location and catalogue number of each piece of equipment.

**C408.3.2.2 Manuals.** An operating and maintenance manual shall be provided and include the following:

1. Name and address of not less than one service agency for installed equipment.
2. A narrative of how each system is intended to operate, including recommended setpoints.
3. Submittal data indicating all selected options for each piece of lighting equipment and lighting controls.
4. Operation and maintenance manuals for each piece of lighting equipment. Required routine maintenance actions, cleaning and recommended relamping shall be clearly identified.
5. A schedule for inspecting and recalibrating all lighting controls.

**C408.3.2.3 Report.** A report of test results shall be provided and include the following:

1. Results of functional performance tests.
2. Disposition of deficiencies found during testing, including details of corrective measures used or proposed.

SECTION C409—CALCULATION OF THE HVAC TOTAL SYSTEM PERFORMANCE RATIO

**C409.1 Applicability.** Use of the *HVAC total system performance ratio* (TSPR) method shall comply with this section.

**C409.2 Permitted uses.** Only HVAC systems that serve building occupancies and uses in Table C409.4 and are not excluded by Section C409.2.1 shall be permitted to use the TSPR method.

**C409.2.1 Systems not permitted.** The following HVAC systems are not permitted to use Section C403.1, Item 3:

* 1. HVAC systems using:
     1. District heating water, chilled water or steam.
     2. Small-duct high-velocity air-cooled, space-constrained air-cooled, or single-package verti- cal air conditioner; single-package vertical heat pump; or double-duct air conditioner or double-duct heat pump, as defined in subpart F to 10 CFR Part 431.
     3. Packaged terminal air conditioners and packaged terminal heat pumps that have a cooling capacity greater than 12,000 Btu/h (3.5 kW).
     4. A common heating source serving both HVAC and *service water heating* equipment.
  2. HVAC systems that provide recovered heat for *service water heating.*
  3. HVAC systems not specified in Table C409.6.1.10.1.
  4. HVAC systems specified in Table C409.6.1.10.1 with characteristics or parameters in Table C409.6.1.10.2(1), not identified as applicable to that HVAC system type.
  5. HVAC systems with chilled water supplied by absorption chillers, heat recovery chillers, water-to-water heat pumps, air- to-water heat pumps, or a combination of air- and water-cooled chillers on the same chilled water loop.
  6. HVAC systems served by heating water systems that include air-to-water or water-to-water heat pumps.
  7. Underfloor air distribution and displacement ventilation HVAC systems.
  8. Space-conditioning systems that do not include mechanical cooling.
  9. HVAC systems serving laundry rooms, elevator rooms, mechanical rooms, electrical rooms, *data centers* and *computer rooms*.
  10. *Buildings* or areas of medical office buildings required to use ASHRAE Standard 170.
  11. *Buildings* or areas that are required by regulation to have continuous air-handling unit operation.
  12. HVAC systems serving laboratories with fume hoods.
  13. Locker rooms with more than two showers.
  14. Natatoriums and rooms with saunas.
  15. Restaurants and commercial kitchens with a total cooking capacity greater than 100,000 Btu/h (29 kW).
  16. Areas of *buildings* with commercial refrigeration equipment exceeding 100 kW of power input.
  17. Cafeterias and dining rooms

**C409.3 HVAC TSPR compliance.** HVAC systems permitted to use TSPR shall comply with Section C409.4 and the following:

1. HVAC systems shall comply with applicable requirements of Section C403 as follows:
   1. Air economizers shall meet the requirements of Sections C403.5.3.4 and C403.5.5.
   2. Variable-air-volume systems shall meet the requirements of Sections C403.6.5, C403.6.6 and C403.6.9.
   3. Hydronic systems shall meet the requirements of Section C403.4.4.
   4. Plants with multiple chillers or boilers shall meet the requirements of Section C403.4.5.
   5. Hydronic (water loop) heat pumps and water-cooled unitary air conditioners shall meet the requirements of Section C403.4.3.3.
   6. Cooling tower turndown shall meet the requirements of Section C403.11.4.
   7. Heating of unenclosed spaces shall meet the requirements of Section C403.14.1.
   8. Hot-gas bypass shall meet the requirements of Section C403.3.3.
   9. Systems shall meet the operable openings interlock requirements of Section C403.4.7. Refrigeration systems shall meet the requirements of Section C403.12.
2. Systems shall comply with the applicable provisions of Section C403 required by Table C407.2.

**C409.4 Performance target.** For HVAC systems serving uses or portions of uses listed in Section C409.2 that are not served by systems listed in Section C409.2.1, the *HVAC TSPR* of the *proposed design* shall be greater than or equal to the *HVAC TSPR* of the *stan- dard reference design* divided by the mechanical performance factor (MPF) using Equation 4-35.

**Equation 4-35** *TSPRp* > *TSPRr*/*MPF*

where:

*TSPRp* = HVAC TSPR of the proposed design calculated in accordance with Sections C409.4, C409.5 and C409.6.

*TSPRr* = HVAC TSPR of the reference building design calculated in accordance with Sections C409.4, C409.5 and C409.6.

*MPF* = Mechanical performance factor from Table C409.4 based on climate zone and building use type.

**Equation 4-36** *MPF* = (*A*1 × *MPF*1 + *A*2 × *MPF*2 + *An* × *MPFn*)/(*A*1 + *A*2 + *An*)

where:

*MPF*1, *MPF*2 through *MPFn* = Mechanical performance factors from Table C409.4 based on climate zone and building use types 1, 2 through *n*.

*A*1, *A*2 through *An* = Conditioned floor areas for building use types 1, 2 through *n*.

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE C409.4—MECHANICAL PERFORMANCE FACTORS** | | | | | | | | | | | | | | | | | | | | |
| **BUILDING USE** | **OCCUPANCY GROUP** | **CLIMATE ZONE** | | | | | | | | | | | | | | | | | | |
| **0A** | **0B** | **1A** | **1B** | **2A** | **2B** | **3A** | **3B** | **3C** | **4A** | **4B** | **4C** | **5A** | **5B** | **5C** | **6A** | **6B** | **7** | **8** |
| Office  (all others)a | B | 0.72 | 0.715 | 0.70 | 0.705 | 0.685 | 0.65 | 0.71 | 0.68 | 0.645 | 0.805 | 0.70 | 0.78 | 0.845 | 0.765 | 0.805 | 0.865 | 0.835 | 0.875 | 0.895 |
| Office (large)a | B | 0.83 | 0.83 | 0.84 | 0.84 | 0.79 | 0.82 | 0.72 | 0.81 | 0.77 | 0.67 | 0.76 | 0.63 | 0.71 | 0.72 | 0.63 | 0.73 | 0.71 | 0.71 | 0.71 |
| Retail | M | 0.60 | 0.57 | 0.50 | 0.55 | 0.46 | 0.46 | 0.43 | 0.51 | 0.40 | 0.45 | 0.57 | 0.68 | 0.46 | 0.68 | 0.67 | 0.50 | 0.45 | 0.44 | 0.38 |
| Hotel/motel | R-1 | 0.62 | 0.62 | 0.63 | 0.63 | 0.62 | 0.68 | 0.61 | 0.71 | 0.73 | 0.45 | 0.59 | 0.52 | 0.38 | 0.47 | 0.51 | 0.35 | 0.38 | 0.31 | 0.26 |
| Multi-family/ dormitory | R-2 | 0.64 | 0.63 | 0.67 | 0.63 | 0.65 | 0.64 | 0.59 | 0.72 | 0.55 | 0.53 | 0.50 | 0.44 | 0.54 | 0.47 | 0.38 | 0.55 | 0.50 | 0.51 | 0.47 |
| School/ education and libraries | E (A-3) | 0.82 | 0.81 | 0.80 | 0.79 | 0.75 | 0.72 | 0.71 | 0.72 | 0.67 | 0.73 | 0.72 | 0.68 | 0.82 | 0.73 | 0.61 | 0.89 | 0.80 | 0.83 | 0.77 |
| a. Large-office conditioned floor area greater than 150,000 square feet or more than five stories. | | | | | | | | | | | | | | | | | | | | |

**C409.4.1 HVAC TSPR.** *HVAC TSPR* is calculated according to Equation 4-37.

**Equation 4-37** HVAC TSPR = heating and cooling load/building HVAC system energy where:

Building HVAC system energy = Sum of the annual site energy consumption for heating, cooling, fans, energy recovery, pumps and heat rejection in thousands of Btu (kWh).

Heating and cooling load = Sum of the annual heating and cooling loads met by the building HVAC system in thousands of Btu (kWh).

**C409.5 General.** Projects shall use the procedures of this section when calculating compliance using HVAC total system performance ratio.

**C409.5.1 Simulation program.** Simulation tools used to calculate the *HVAC TSPR* of the *standard reference design* shall comply with the following:

1. The simulation program shall calculate the *HVAC TSPR* based only on the input for the *proposed design* and the require- ments of Section C409. The calculation procedure shall not allow the user to directly modify the building component characteristics of the *standard reference design*.
2. Performance analysis tools shall meet the applicable subsections of Section C409 and be tested in accordance with ASHRAE Standard 140, except for Sections 7 and 8. The required tests shall include the *building thermal envelope* and fabric load test (Sections 5.2.1, 5.2.2 and 5.2.3), ground-coupled slab-on-grade analytical verification tests (Section 5.2.4), space-cooling equipment performance tests (Section 5.3), space-heating equipment performance tests (Section 5.4), and air-side HVAC equipment analytical verification test (Section 5.5), along with the associated reporting (Section 6).
3. The test results and modeler reports shall be publicly available and shall include the test results of the simulation programs and input files used for generating the results along with the results of the other simulation programs included in ASHRAE Standard 140, Annexes B8 and B16. The modeler report in ASHRAE Standard 140 Annex A2 Attachment A2.7 shall be completed for results exceeding the maximum or falling below the minimum of the reference values and for omitted results.
4. The simulation program shall have the ability to model part-load performance curves or other part-load adjustment methods based on manufacturer’s part-load performance data for mechanical equipment.
5. The *code official* shall be permitted to approve specific software deemed to meet these requirements in accordance with Section C101.4.1.

**C409.5.2 Climatic data.** The simulation program shall perform the simulation using hourly values of climatic data for a full calen- dar year (8,760 hours) and shall reflect *approved* coincident hourly data for temperature, solar radiation, humidity and wind speed for the building location.

**C409.5.3 Documentation.** Documentation or web links to documentation conforming to the provisions of this section shall be provided to the *code official*.

**C409.5.3.1 Compliance report.** Building permit submittals shall include:

* 1. A report produced by the simulation software that includes the following:
     1. Address of the *building*.
     2. Name of the individual completing the compliance report.
     3. Name and version of the compliance software tool.
     4. The dimensions, floor heights and number of floors for each *thermal block*.
     5. By thermal block, the *U-factor*, *C-factor* or *F-factor* for each simulated opaque envelope component and the

*U-factor* and SHGC for each *fenestration* component.

* + 1. By *thermal block* or by surface for each *thermal block*, the *fenestration* area.
    2. By *thermal block*, a list of the HVAC equipment simulated in the *proposed design,* including the equipment type, fuel type, equipment efficiencies and system controls.
    3. Annual site HVAC energy use by end use for the proposed and baseline building.
    4. Annual sum of heating and cooling loads for the baseline building.
    5. The *HVAC TSPR* for both the *standard reference design* and the *proposed design*.
  1. A mapping of the actual *building* HVAC component characteristics and those simulated in the *proposed design* show- ing how individual pieces of HVAC equipment identified in Item 1 have been combined into average inputs as required by Section C409.6.1.10, including:
     1. Fans.
     2. Hydronic pumps.
     3. Air handlers.
     4. Packaged cooling equipment.
     5. Furnaces.
     6. Heat pumps.
     7. Boilers.
     8. Chillers.
     9. Heat rejection equipment (open- and closed-circuit cooling towers, dry coolers).
     10. Electric resistance coils.
     11. Condensing units.
     12. Motors for fans and pumps.
     13. Energy recovery devices.
  2. For each piece of equipment identified in Item 2, include the following, as applicable:
     1. Equipment name or tag consistent with that found on the design documents.
     2. Rated efficiency level.
     3. Rated capacity.
     4. Where not provided by the simulation program report in Item 1, documentation of the calculation of any weighted equipment efficiencies input into the program.
     5. Electrical input power for fans and pumps (before any speed or frequency control device) at design condi- tion and calculation of input value (W/cfm or W/gpm) or W/gpm (W/Lps).
  3. Floor plan of the *building,* identifying:
     1. How portions of the *buildings* are assigned to the simulated thermal blocks.
     2. Areas of the *building* that are not covered under the requirements of Section C403.1.1.

**C409.6 Calculation procedures.** Except as specified by this section, the *standard reference design* and *proposed design* shall be configured and analyzed using identical methods and techniques.

**C409.6.1 Simulation of the proposed building design.** The *proposed design* shall be configured and analyzed as specified in this section.

**C409.6.1.1 Thermal block geometry.** The geometry of *buildings* shall be configured using one or more thermal blocks. Each *thermal block* shall define attributes, including *thermal block* dimensions, number of floors, floor-to-floor height and floor-to- ceiling height. Simulation software may allow the use of simplified shapes (such as rectangle, L-shaped, H-shaped, U-shaped or T-shaped) to represent thermal blocks. Where actual building shape does not match these predefined shapes, simplifica- tions are permitted, provided that the following requirements are met:

1. The *conditioned floor area* and volume of each *thermal block* shall match the *proposed design* within 10 percent.
2. The area of each exterior envelope component from Table C402.1.4 is accounted for within 10 percent of the actual design.
3. The area of vertical *fenestration* and skylights is accounted for within 10 percent of the actual design.
4. The orientation of each component in Items 2 and 3 is accounted for within 45 degrees of the actual design.

The creation of additional *thermal blocks* may be necessary to meet these requirements. A more complex zoning of the *building* shall be allowed where all *thermal zones* in the reference and proposed models are the same, and rules related to ther- mal block geometry and HVAC system assignment to *thermal blocks* are met with appropriate assignment to thermal zones.

**Exception:** Portions of the *building* that are unconditioned or served by systems not covered by the requirements of Section C403.1.1 shall be omitted.

**C409.6.1.1.1 Number of thermal blocks.** One or more *thermal blocks* may be required per *building* based on the following restrictions:

* 1. Each *thermal block* shall have not more than one building use.
  2. Each *thermal block* shall be served by not more than one type of HVAC system. A single block shall be created for each unique HVAC system and building use combination, and multiple HVAC units or components of the same type shall be combined in accordance with Section C409.6.1.10.2.
  3. Each *thermal block* shall have not more than a single defined floor-to-floor or floor-to-ceiling height. Where floor heights differ by more than 2 feet, separate thermal blocks shall be created.
  4. Each block shall include either above-grade or below-grade stories. For *buildings* with both above-grade and below-grade stories, separate blocks shall be created for each. Where blocks have *exterior walls* partially below grade, if greater than 50 percent of the exterior wall surface is below grade, then simulate the block as below grade; otherwise, simulate as above grade.
  5. Where a block includes multiple stories, separate blocks shall be created, if needed, to comply with both the following *fenestration* modeling requirements:
     1. The product of the *proposed design U-factor* times the area of windows (*U* × *A*) on a given story of each facade shall not differ by more than 15 percent of the average *U* × *A* for that modeled facade in each block.
     2. The product of the *proposed design* SHGC times the area of windows (SHGC × *A*) on a given story of each facade shall not differ by more than 15 percent of the average SHGC × *A* for that modeled facade in each block.
  6. For a building model with multiple blocks, the blocks shall be configured together to have the same adjacencies as the actual building design.

**C409.6.1.2 Thermal zoning.** Each story in a *thermal block* shall be modeled as follows:

1. Below-grade stories shall be modeled as a single thermal zone.
2. Where any facade in the block is less than 45 feet (13.7 m) in length, it shall be modeled as a single thermal zone per story.
3. For stories not covered by Item 1 or Item 2, each story shall be modeled with five thermal zones. A perimeter zone shall be created, extending from each facade to a depth of 15 feet (4572 mm). Where facades intersect, the zone boundary shall be formed by a 45-degree angle with the two facades. The remaining area of each story shall be modeled as a core zone with no *exterior walls*.

**C409.6.1.2.1 Core and shell, build-out and future system construction analysis.** Where the building permit applies to only a portion of the HVAC system in a *building* and the remaining components will be designed under a future building permit or were previously installed, such components shall be modeled as follows:

* 1. Blocks including existing or future HVAC *zone* served by independent systems and not part of the construction project shall not be modeled.
  2. Where the HVAC *zones* that do not include complete HVAC systems in the permit are intended to receive HVAC services from systems that are part of the construction project, their proposed zonal systems shall be modeled with equipment that meets, but does not exceed, the requirements of Section C403.
  3. Where existing HVAC systems serve permitted *zone* equipment, the existing systems shall be modeled with equip- ment matching the manufacturer’s stated efficiency for the installed equipment or equipment that meets, but does not exceed, the requirements of Section C403.
  4. Where the central plant heating and cooling equipment is completely replaced and HVAC *zones* with existing systems receive HVAC services from systems in the permit, their proposed zonal systems shall be modeled with equipment that meets, but does not exceed, the requirements of Section C403.

**C409.6.1.3 Occupancy.** Building occupancies modeled in the *standard reference design* and the *proposed design* shall comply with the following requirements.

**C409.6.1.3.1 Occupancy type.** The occupancy type for each *thermal block* shall be consistent with the building occupancy and uses specified in Table C409.4. Portions of the building occupancy and uses other than those specified in Table C409.4 shall not be included in the simulation. Surfaces adjacent to such excluded *building* portions shall be modeled as adiabatic in the simulation program.

**C409.6.1.3.2 Occupancy schedule, density and heat gain.** The occupant density, heat gain and schedule shall be for multi- family, offices, retail spaces, libraries, hotels/motels or schools as specified by ANSI/ASHRAE/IES 90.1, Normative Appendix C.

**C409.6.1.4 Building thermal envelope components.** *Building thermal envelope* components modeled in the *standard refer- ence design* and the *proposed design* shall comply with the requirements of this section.

**C409.6.1.4.1 Roofs.** The roof *U-factor* and area shall be modeled as in the *proposed design*. If different roof thermal proper- ties are present in a single *thermal block*, an area-weighted *U-factor* shall be used. Roofs shall be modeled with insulation above a steel roof deck, with a solar reflectance of 0.25 and an *emittance* of 0.90.

**Exception:** For Climate Zones 0, 1, 2 and 3, solar reflectance and *emittance* shall be as specified in Section C402.4 and Table C402.4.

**C409.6.1.4.2 Above-grade walls.** The *U-factor* and area of *above-grade walls* shall be modeled as in the *proposed design*. If different wall constructions exist on the facade of a thermal block, an area-weighted *U-factor* shall be used. Walls will be modeled as steel-frame construction.

**C409.6.1.4.3 Below-grade walls.** The *C-factor* and area of *below-grade walls* shall be modeled as in the *proposed design*. If different *below-grade wall* constructions exist in a *thermal block*, an area-weighted *C-factor* shall be used.

**C409.6.1.4.4 Above-grade exterior floors.** The *U-factor* and area of floors shall be modeled as in the *proposed design*. If different floor constructions exist in the *thermal block*, an area-weighted *U-factor* shall be used. Exterior floors shall be modeled as steel frame.

**C409.6.1.4.5 Slab-on-grade floors.** The *F-factor* and perimeter of slab-on-grade floors shall be modeled as in the *proposed design*. If different slab-on-grade floor constructions exist in a *thermal block*, a perimeter-weighted *F-factor* shall be used.

**C409.6.1.4.6 Vertical fenestration.** The window area and area-weighted *U-factor* and SHGC shall be modeled for each facade based on the *proposed design*. Each exterior surface in a *thermal block* must comply with Section C409.6.1.1.1, Item

* 1. Windows shall be combined into a single window centered on each facade based on the area and sill height input by the user. Where different *U*-*values*, SHGC or sill heights exist on a single facade in a block, the area-weighted average for each shall be input by the user.

**C409.6.1.4.7 Skylights.** The skylight area and area-weighted *U-factor* and SHGC shall be modeled for each roof based on the *proposed design*. Skylights shall be combined into a single skylight centered on the roof of each zone based on the area input by the user.

**C409.6.1.4.8 Exterior shading.** Permanent window overhangs shall be modeled. Where windows with and without over- hangs or windows with different overhang projection factors exist on a facade, window width-weighted projection factors shall be input by the user as follows:

**Equation 4-38** *Pavg* = (*A*1 × *Lo*1 + *A*2 ×*Lo*2 *An* × *Lon*)/(*Lw*1 + *Lw*2 *Lwn*

where:

*Pavg* = Average overhang projection modeled in the simulation tool.

*A* = Distance measured horizontally from the farthest continuous extremity of any overhang, eave or permanently attached shading device to the vertical surface of the glazing.

*L*o = Length off the overhang.

*Lw* = Length of the window.

**C409.6.1.5 Lighting.** Interior lighting power density shall be equal to the allowance in Table C405.3.2(1) for multifamily build- ings, offices, retail spaces, libraries or schools. The lighting schedule shall be for multifamily buildings, offices, retail spaces, libraries or schools as specified by ANSI/ASHRAE/IES 90.1, Normative Appendix C. The impact of lighting controls is assumed to be captured by the lighting schedule and no explicit controls shall be modeled. Exterior lighting shall not be modeled.

**C409.6.1.6 Miscellaneous equipment.** The miscellaneous equipment schedule and power shall be for multifamily buildings, offices, retail spaces, libraries or schools as specified by ANSI/ASHRAE/IES 90.1, Normative Appendix C. The impact of miscella- neous equipment controls is assumed to be captured by the equipment schedule and no explicit controls shall be modeled.

Exceptions:

* + 1. Multiple-family dwelling units shall have a miscellaneous load density of 0.42 watts per square foot.
    2. Multiple-family *common areas* shall have a miscellaneous load density of 0 watts per square foot.

**C409.6.1.7 Elevators.** Elevators shall not be modeled.

**C409.6.1.8 Service water heating equipment.** *Service water heating* shall not be modeled.

**C409.6.1.9 On-site renewable energy systems.** On-site renewable energy systems shall not be modeled.

**C409.6.1.10 HVAC equipment.** Where proposed or where reference system parameters are not specified in Section C409, HVAC systems shall be modeled to meet the minimum requirements of Section C403.

**C409.6.1.10.1 Supported HVAC systems.** At a minimum, the HVAC systems shown in Table C409.6.1.10.1 shall be supported by the simulation program.

|  |  |
| --- | --- |
| **TABLE C409.6.1.10.1—PROPOSED BUILDING HVAC SYSTEMS SUPPORTED BY HVAC TSPR SIMULATION SOFTWARE** | |
| **SYSTEM NO.** | **SYSTEM NAME** |
| 1 | Packaged terminal air conditioner (with electric or hydronic heat) |
| 2 | Packaged terminal air heat pump |
| 3 | Packaged single-zone gas furnacea and/or air-cooled air conditioner (includes split systems)b |
| 4 | Packaged single-zone heat pump (air to air only)(includes split systemsb and electric or gas supplemental heat) |
| 5 | Variable refrigerant flow (air cooled only) |
| 6 | Four pipe fan coil |
| 7 | Water-source heat pump (water loop), water-source v*ariable refrigerant flow system* or water-source air conditioner |
| 8 | Ground source heat pump |
| 9 | Packaged variable air volume (DX cooling)a |
| 10 | Variable air volume (hydronic cooling)a |
| 11 | Variable air volume with fan-powered terminal units |
| 12 | Dedicated outdoor air system (in conjunction with systems 1–8) |
| 1. Reheat or primary heat may be electric, hydronic or gas furnace. 2. Condensing units with DX air handlers are modeled as package furnaces with air conditioners or heat pumps. | |

**C409.6.1.10.2 Proposed building HVAC system simulation.** The HVAC systems shall be modeled as in the *proposed design* at design conditions unless otherwise stated, with clarifications and simplifications as described in Tables C409.6.1.10.2(1) and C409.6.1.10.2(2). System parameters not described in the following sections shall be simulated to meet the minimum requirements of Section C403. All *zones* within a thermal block shall be served by the same HVAC system type as described in Section C409.6.1.1.1, Item 2. Heat loss from *ducts* and pipes shall not be modeled. The proposed building system param- eters in Table C409.6.1.10.2(1) are based on input of full-load equipment efficiencies with adjustments using part-load curves integrated into the simulation program. Where other approaches to part-load adjustments are used, it is permitted for specific input parameters to vary. The simulation program shall model part-load HVAC equipment performance using one of the following:

1. Full-load efficiency adjusted for fan power input that is modeled separately and typical part-load performance adjustments for the proposed equipment.
2. Part-load adjustments based on input of both full-load and part-load metrics.
3. Equipment-specific adjustments based on performance data provided by the equipment manufacturer for the proposed equipment.

Where multiple system components serve a thermal block, average values weighted by the appropriate metric as described in this section shall be used.

1. Where multiple fan systems serve a single thermal block, fan power shall be based on a weighted average using the design supply air (cfm).
2. Where multiple cooling systems serve a single thermal block, the coefficient of performance (COP) shall be based on a weighted average using cooling capacity. Direct expansion (DX) coils shall be entered as multistage if more than 50 percent of coil capacity serving the thermal block is multistage with staged controls.
3. Where multiple heating systems serve a single thermal block, thermal efficiency or heating COP shall be based on a weighted average using heating capacity.
4. Where multiple boilers or chillers serve a heating water or chilled water loop, efficiency shall be based on a weighted average for using heating or cooling capacity.
5. Where multiple cooling towers serving a condenser water loop are combined, the cooling tower efficiency, cooling tower design approach and design range are based on a weighted average of the design water flow rate through each cooling tower.
6. Where multiple pumps serve a heating water, chilled water or condenser water loop, pump power shall be based on a weighted average for using design water flow rate.
7. Where multiple system types with and without economizers are combined, the economizer maximum outside air fraction of the combined system shall be based on the weighted average of 100 percent supply air for systems with economizers and design outdoor air for systems without economizers.
8. Multiple systems with and without ERVs cannot be combined.
9. Systems with and without supply-air temperature reset controls cannot be combined.
10. Systems with different fan controls (constant volume, multispeed or VAV) for supply fans cannot be combined.

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **TABLE C409.6.1.10.2(1)—PROPOSED BUILDING SYSTEM PARAMETERS** | | | | |
| **CATEGORY** | **PARAMETER** | **FIXED OR USER DEFINED** | **REQUIRED** | **APPLICABLE SYSTEMS** |
| HVAC system type | System type | User defined | Selected from Table C409.6.1.10.1 | All |
| System sizing | Design day information | Fixed | 99.6% heating design and 1% dry-bulb and 1% wet-bulb cooling design | All |
| Zone coil capacity | Fixed | Sizing factors used are 1.25 for heating equip- ment and 1.15 for cooling equipment | All |
| Supply airflow | Fixed | Based on a supply-air-to-room-air temperature setpoint difference of 20°F (11.2°C) | 1–11 |
| Fixed | Equal to required outdoor air ventilation | 12 |
| Outdoor ventilation air | Portion of supply air with proposed filter ≥ MERV 13 | User defined | Percentage of supply airflow subject to higher filtration (adjusts baseline fan power higher; prorated) | All |
| Outdoor ventilation airflow rate | Fixed | As specified in ANSI/ASHRAE/IES 90.1, Normative Appendix C; adjusted for proposed DCV control | All |
| Outdoor ventilation supply airflow rate adjustments | Fixed | Based on ASHRAE 62.1 Section 6.2.4.3, system ventilation efficiency (Ev) is 0.75 | 9–11 |
| Fixed | System ventilation efficiency (Ev) is 1.0 | 1–8, 12 |
| Fixed | Basis is 1.0 zone air distribution effectiveness | All |
| System operation | Space temperature setpoints | Fixed | As specified in ANSI/ASHRAE/IES 90.1, Normative Appendix C, except:   * Multiple-family, which shall use 68°F heating and 76°F cooling setpoints. * Hotel/motel setpoints, which shall be 70°F heating and 72°F cooling. | 1–11 |
| Fan operation—occupied | User defined | Runs continuously during occupied hours or cycles to meet load. Multispeed fans reduce airflow related to thermal loads. | 1–11 |
| Fan operation—occupied | Fixed | Fan runs continuously during occupied hours | 12 |
| Fan operation—night cycle | Fixed | Fan cycles on to meet setback temperatures | 1–11 |
| Packaged equipment efficiency | DX cooling efficiency | User defined | Cooling COP without fan energy calculated in accordance with Section C409.6.1.10.2 | 1, 2, 3, 4, 5,7,  8, 9, 11,12 |
| DX coil number of stages | User defined | Single stage or multistage | 3, 4, 9, 10, 11,  12 |
| Heat pump efficiency | User defined | Heating COP without fan energy calculated in accordance with Section C409.6.1.10.2 | 2, 4, 5, 7, 8, 12 |
| Furnace efficiency | User defined | Furnace thermal efficiency | 3, 9, 11, 12 |
| Heat pump supple- mental heat | Heat source | User defined | Electric resistance or gas furnace | 2, 4, 7, 8, 12 |
| Control | Fixed | Supplemental electric heat locked out above 40°F OAT. Runs as needed in conjunction with compressor between 40°F and 0°F. Gas heat oper- ates in place of the heat pump when the heat pump cannot meet load. | 2, 4, 7, 8, 12 |
| System fan power and controls | Part-load fan controlsa:   * Constant volume. * Two speed or three speed. * VAV. | User defined | Static pressure reset included for VAV | 1–8 (CAV, two  or three speed), 9, 10,  11 (VAV), 12 (CAV and VAV) |
| Design fan power (W/cfm) | User defined | Input electric power for all fans required to oper- ate at fan system design conditions divided by the supply airflow rate. This is a wire-to-air value, including all drive, motor efficiency and other losses. | All |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **TABLE C409.6.1.10.2(1)—PROPOSED BUILDING SYSTEM PARAMETERS—continued** | | | | |
| **CATEGORY** | **PARAMETER** | **FIXED OR USER DEFINED** | **REQUIRED** | **APPLICABLE SYSTEMS** |
| System fan power and controls—continued | Low-speed and medium- speed fan power | User defined | Low-speed input electric power for all fans required to operate at low-speed conditions divided by the low-speed supply airflow rate. This is a wire-to-air value, including all drive, motor efficiency and other losses. Also provide medium- speed values for three-speed fans. | 1-8 |
| Variable air volume systems | Supply air temperature (SAT) controls | User defined | If not SAT reset, then constant at 55°F. Options for reset based on OAT or warmest zone. If warmest zone, then the user can specify the minimum and maximum temperatures. If OAT reset, SAT is reset higher to 60°F at an outdoor low of 50°F. SAT is 55°F at an outdoor high of 70°F. | 9, 10, 11 |
| Minimum terminal unit airflow percentage | User defined | Average minimum terminal unit airflow percent- age for thermal block weighted by cfm or minimum required for outdoor air ventilation, whichever is higher. | 9, 10, 11 |
| Terminal unit heating source | User defined | Electric or hydronic | 9, 10, 11 |
| Dual setpoint minimum VAV damper position | User defined | Heating maximum airflow fraction | 9, 10 |
| Fan-powered terminal unit (FPTU) type | User defined | Series or parallel FPTU | 11 |
| Parallel FPTU fan | Fixed | Sized for 50% peak primary air at 0.35 W/cfm | 11 |
| Series FPTU fan | Fixed | Sized for 50% peak primary air at 0.35 W/cfm | 11 |
| Economizer | Economizer presence | User defined | Yes or no | 3, 4, 5, 6, 9, 10,  11 |
| Economizer control type | Fixed | Lockout on differential db temperature  (OAT > RAT) in Climate Zones 5A, 6A, all B & C; fixed enthalpy > 28 Btu/lb (47kJ/kg) or fixed db OAT > 75°F (24°C) in Climate Zones 0A through 4A | 3, 4, 5, 6, 9, 10,  11 |
| Energy recovery | Sensible effectiveness | User defined | Heat exchanger sensible effectiveness at design heating and cooling conditions | 3, 4, 9, 10, 11,  12 |
| Latent effectiveness | User defined | Heat exchanger latent effectiveness at design heating and cooling conditions | 3, 4, 9, 10, 11,  12 |
| Economizer bypass | User defined | If ERV is bypassed or wheel rotation is slowed during economizer conditions (yes/no) | 3, 4, 9, 10, 11,  12 |
| Economizer bypass active | Fixed | If there is a bypass, it will be active between 45°F and 75°F outside air temperature | 3, 4, 9, 10, 11,  12 |
| Bypass SAT setpoint | User defined | If bypass, target SAT | 3, 4, 9, 10, 11,  12 |
| Fan power reduction during bypass (W/cfm) | User defined | If ERV system includes bypass, static pressure setpoint and variable speed fan, fan power can be reduced during economizer conditions | 3, 4, 9, 10, 11,  12 |
| Demand control ventilation (DCV) | DCV application on/off | User defined | Percent of thermal block floor area under occu- pied standby controls, on/off only with occupancy sensor and no variable control | 3, 4, 9, 10, 11,  12 |
| DCV application CO2 | User defined | Percentage of thermal block floor area under variable DCV control (CO2); may include both vari- able and on/off controls | 3, 4, 9, 10, 11,  12 |
| DOAS | DOAS fan power W/cfm | User defined | Fan electrical input power in W/cfm of supply airflow | 12 |
| DOAS supplemental heating and cooling | User defined | Heating source, cooling source, energy recovery and respective efficiencies | 12 |
| Maximum SAT setpoint (cooling) | User defined | SAT setpoint if DOAS includes supplemental cooling | 12 |
| Minimum SAT setpoint (heating) | User defined | SAT setpoint if DOAS includes supplemental heating | 12 |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **TABLE C409.6.1.10.2(1)—PROPOSED BUILDING SYSTEM PARAMETERS—continued** | | | | |
| **CATEGORY** | **PARAMETER** | **FIXED OR USER DEFINED** | **REQUIRED** | **APPLICABLE SYSTEMS** |
| Heating plant | Boiler efficiency | User defined | Boiler thermal efficiency | 1, 6, 7, 9, 10,  11, 12 |
| Heating water loop configuration | User defined | Constant flow primary only; variable flow primary only; constant flow primary/variable flow secondary; variable flow primary and secondary | 1, 6, 7, 9, 10,  11, 12 |
| Heating water primary pump power (W/gpm) | User defined | Heating water primary pump input W/gpm heat- ing water flow | 1, 6, 7, 9, 10,  11, 12 |
| Heating water secondary pump power (W/gpm) | User defined | Heating water secondary pump input W/gpm heating water flow (if primary/secondary) | 1, 6, 7, 9, 10,  11, 12 |
| Heating water loop temperature | User defined | Heating water supply and return temperatures, °F | 1, 6, 9, 10,11 |
| Heating water loop supply temperature reset | Fixed | Reset HWS by 27.3% of design delta-T (HWS-70°F space heating temperature setpoint) between 20°F and 50°F OAT | 1, 6, 7, 9, 10,  11, 12 |
| Boiler type | Fixed | Noncondensing boiler where input thermal effi- ciency is less than 86%; condensing boiler otherwise | 1, 6, 7, 9, 10,  11, 12 |
| Chilled water plant | Chiller compressor type | User defined | Screw/scroll, centrifugal or reciprocating | 6, 10, 11, 12 |
| Chiller condenser type | User defined | Air cooled or water cooled | 6, 10, 11, 12 |
| Chiller full-load efficiency | User defined | Chiller COP | 6, 10, 11, 12 |
| Chilled water loop configuration | User defined | Variable flow primary only, constant flow primary/variable flow secondary, variable flow primary and secondary | 6, 10, 11,12 |
| Chilled water primary pump power (W/gpm) | User defined | Primary pump input W/gpm chilled water flow | 6, 10, 11,12 |
| Chilled water secondary pump power (W/gpm) | User defined | Secondary pump input W/gpm chilled water flow (if primary/secondary) | 6, 10, 11,12 |
| Chilled water temperature reset included | User defined | Yes/no | 6, 10, 11,12 |
| Chilled water temperature reset schedule (if included) | Fixed | Outdoor air reset: CHW supply temperature of 44°F at 80°F (26.7°C) outdoor air db temperature and above, CHW supply temperature of 54°F at 60°F outdoor air db temperature and below, ramped linearly between | 6, 10, 11,12 |
| Condenser water pump power (W/gpm) | User defined | Pump input W/gpm condenser water flow | 6, 7, 8, 10, 11,  12 |
| Condenser water pump control | User defined | Constant speed or variable speed | 6, 7, 8, 10,  11,12 |
| Heat rejection equipment efficiency | User defined | Gpm/hp tower fan | 6, 7, 10, 11, 12 |
| Heat rejection fan control | User defined | Constant or variable speed | 6, 7, 10, 11, 12 |
| Heat rejection approach and range | User defined | Design cooling tower approach and range temperature | 6, 7, 10, 11, 12 |
| Heat pump loop | Loop flow and heat pump control valve | Fixed | Two-position valve with VFD on pump; loop flow at 3 gpm/ton | 7, 8 |
| Heat pump loop minimum and maximum temperature control | User defined | User input: restrict to minimum 20°F and maxi- mum 40°F temperature difference | 7 |
| GLHP well field | — | Fixed | Bore depth = 250 ft  Bore length 200 ft/ton for the greater of cooling or heating load  Bore spacing = 15 ft Bore diameter = 5 in  ¾″ (19 mm) polyethylene pipe  Ground and grout conductivity = 4.8 Btu × in/h × ft2 × °F | 8 |
| For SI: 1 inch = 25.4 mm, 1 foot = 304.8 mm, °C = (°F – 32)/1.8, 1 British thermal unit per hour = 0.2931 W, 1 British thermal unit per pound = 2.33 kJ/kg, 1 cubic foot per minute = 0.4719 L/s, 1 cubic foot per minute/foot = 47.82 W, COP = (Btu/h × hp)/(2,550.7), 1 gallon per minute = 3.79 L/m.  CHW =Chilled Water, db = dry bulb, DOAS = Dedicated Outdoor Air System, GLHP = Ground Loop Heat Pump, HWS = Hot Water Supply, OAT = Outdoor Air Temperature, SAT = Supply Air Temperature, VFD = Variable Frequency Drive, wb = wet bulb.  a. Part-load fan power and pump power modified in accordance with Table C409.6.1.10.2(2). | | | | |

|  |  |  |  |
| --- | --- | --- | --- |
| **TABLE C409.6.1.10.2(2)—FAN AND PUMP POWER CURVE COEFFICIENTS** | | | |
| **EQUATION TERM** | **FAN POWER COEFFICIENTS** | **PUMP POWER COEFFICIENTS** | |
| **VSD + SP Reset** | **Ride Pump Curve** | **VSD + DP/Valve Reset** |
| *b* | 0.0408 | 0 | 0 |
| *x* | 0.088 | 3.2485 | 0.0205 |
| *x*2 | -0.0729 | -4.7443 | 0.4101 |
| *x*3 | 0.9437 | 2.5295 | 0.5753 |

**C409.6.1.10.3 Demand control ventilation.** Demand control ventilation (DCV) shall be modeled using a simplified approach that adjusts the design outdoor supply airflow rate based on the floor area of the *building* that is covered by DCV. The simplified method shall accommodate both variable DCV and on/off DCV, giving on/off DCV one third of the effective floor control area of the variable DCV. Outdoor air reduction coefficients shall be as stated in Table C409.6.1.10.3.

**Exception:** On/off DCV shall receive full effective area adjustment for R-1 and R-2 occupancies.

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **TABLE C409.6.1.10.3—DCV OUTDOOR AIR REDUCTION CURVE COEFFICIENTS** | | | | |
| **EQUATION TERM** | **DCV OSA REDUCTION (*y*) AS A FUNCTION OF EFFECTIVE DCV CONTROL FLOOR AREA (*x*)** | | | |
| **Office** | **School** | **Hotel, Motel, Multiple- Family, Dormitory** | **Retail** |
| *b* | 0 | 0 | 0 | 0 |
| *x* | 0.4053 | 0.2676 | 0.5882 | 0.4623 |
| *x*2 | -0.8489 | 0.7753 | -1.0712 | -0.848 |
| *x*3 | 1.0092 | -1.5165 | 1.3565 | 1.1925 |
| *x*4 | -0.4168 | 0.7136 | -0.6379 | -0.5895 |
| OSA = Outside Air. | | | | |

**C409.6.2 Simulation of the standard reference design.** The *standard reference design* shall be configured and analyzed as spec- ified in this section.

**C409.6.2.1 Utility rates.** Same as the *proposed design*. **C409.6.2.2 Thermal blocks.** Same as the *proposed design*. **C409.6.2.3 Thermal zoning.** Same as the *proposed design*.

**C409.6.2.4 Occupancy type, schedule, density and heat gain.** Same as the *proposed design*.

**C409.6.2.5 Envelope components.** Same as the *proposed design*

**C409.6.2.6 Lighting.** Same as the *proposed design*.

**C409.6.2.7 Miscellaneous equipment.** Same as the *proposed design*.

**C409.6.2.8 Elevators.** Not modeled. Same as the *proposed design*.

**C409.6.2.9 Service water heating equipment.** Not modeled. Same as the *proposed design*.

**C409.6.2.10 On-site renewable energy systems.** Not modeled. Same as the *proposed design*.

**C409.6.2.11 HVAC equipment.** The reference building design HVAC equipment consists of separate space conditioning systems as described in Tables C409.6.2.11(1) through C409.6.2.11(3) for the appropriate building use types. In these tables, “warm” refers to Climate Zones 0 through 2 and 3A, and “cold” refers to Climate Zones 3B, 3C and 4 through 8.

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **TABLE C409.6.2.11(1)—REFERENCE BUILDING DESIGN HVAC COMPLEX SYSTEMS** | | | | |
| **BUILDING TYPE PARAMETER** | **BUILDING TYPE** | | | |
| **Large Office (warm)** | **Large Office (cold)** | **School (warm)** | **School (cold)** |
| System type | VAV/RH | VAV/RH | VAV/RH | VAV/RH |
| Water-cooled chiller |
| Electric reheat (PIU) | Water-cooled chiller | Water-cooled chiller |
| Gas boiler | Electric reheat (PIU) | Water-cooled chiller |
| Gas boiler |
| Fan control | VSD (no SP reset) | VSD (no SP reset) | VSD (no SP reset) | VSD (no SP reset) |
| Main fan power [W/cfm (W × s/L)] proposed  ≥ MERV 13 | 1.165 (2.468) | 1.165 (2.468) | 1.165 (2.468) | 1.165 (2.468) |
| Main fan power [W/cfm (W × s/L)] proposed  < MERV 13 | 1.066 (2.259) | 1.066 (2.259) | 1.066 (2.259) | 1.066 (2.259) |
| Zonal fan power [W/cfm (W × s/L)] | 0.35 (0.75) | NA | 0.35 (0.75) | NA |
| Minimum zone airflow fraction | 1.5 × Voz | 1.5 × Voz | 1.2 × Voz | 1.2 × Voz |
| Heat/cool sizing factor | 1.25/1.15 | 1.25/1.15 | 1.25/1.15 | 1.25/1.15 |
| Outdoor air economizer | No | Yes except 4A | No | Yes except 4A |
| Occupied OSA (= proposed) | Sum(Voz)/0.75 | Sum(Voz)/0.75 | Sum(Voz)/0.65 | Sum(Voz)/0.65 |
| Energy recovery ventilator efficiency ERR; ERV bypass SAT setpoint | NA | NA | 50%  No bypass | 50%  60°F except 4A |
| DCV | No | No | No | No |
| Cooling source | (2) Water-cooled centrifugal chillers | (2) Water-cooled centrifugal chillers | (2) Water-cooled screw chillers | (2) Water-cooled screw chillers |
| Cooling COP (net of fan) | Path B for profile | Path B for profile | Path B for profile | Path B for profile |
| Heating source (reheat) | Electric resistance | Gas boiler | Electric resistance | Gas boiler |
| Furnace or boiler efficiency | 1.0 | 75% Et | 1.0 | 80% Et |
| Condenser heat rejection | Axial fan open circuit cooling tower | | | |
| Cooling tower efficiency [gpm/fan hp (L/s × fan kW)] | 38.2 | 38.2 | 38.2 | 38.2 |
| Tower turndown [> 300 ton (1060 kW)] | 50% | 50% | 50% | 50% |
| Pump (constant flow/variable flow) | Constant flow; 10°F (5.6°C) range | Constant flow; 10°F (5.6°C) range | Constant flow; 10°F (5.6°C) range | Constant flow; 10°F (5.6°C) range |
| Tower approach | 25.72 – (0.24 × wb), where wb is the 0.4% evaporation design wet-bulb temperature (°F) | | | |
| Cooling condenser pump power [W/gpm (W × s/L)] | 19 (300) | 19 (300) | 19 (300) | 19 (300) |
| Cooling primary pump power [W/gpm (W × s/L)] | 9 (142) | 9 (142) | 9 (142) | 9 (142) |
| Cooling secondary pump power [W/gpm (W × s/L)] | 13 (205) | 13 (205) | 13 (205) | 13 (205) |
| Cooling coil chilled water delta-T, °F (°C) | 12 (6.7) | 12 (6.7) | 12 (6.7) | 12 (6.7) |
| Design chilled water supply temperature,  °F (°C) | 44 (6.7) | 44 (6.7) | 44 (6.7) | 44 (6.7) |
| Chilled water supply temperature (CHWST) reset setpoint vs. outside air temperature (OAT), °F (°C) | CHWST: 44-54/ OAT 80-60  (6.7-12.2/26.7-15.6) | CHWST: 44-54/ OAT 80-60  (6.7-12.2/26.7-15.6) | CHWST: 44-54/ OAT 80-60  (6.7-12.2/26.7-15.6) | CHWST: 44-54/ OAT 80-60  (6.7-12.2/26.7-15.6) |
| CHW cooling loop pumping control | 2-way valves & pump VSD | 2-way valves & pump VSD | 2-way valves & pump VSD | 2-way valves & pump VSD |
| Heating pump power [W/gpm (W × s/L)] | 16.1 (254) | 16.1 (254) | 19 (300) | 19 (300) |
| Heating oil HW dT, °F (°C) | 50 (10) | 50 (10) | 50 (10) | 50 (10) |
| Design hot water supply temperature (HWST), °F (°C) | 180 (82.2) | 180 (82.2) | 180 (82.2) | 180 (82.2) |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **TABLE C409.6.2.11(1)—REFERENCE BUILDING DESIGN HVAC COMPLEX SYSTEMS—continued** | | | | |
| **BUILDING TYPE PARAMETER** | **BUILDING TYPE** | | | |
| **Large Office (warm)** | **Large Office (cold)** | **School (warm)** | **School (cold)** |
| HWST reset setpoint vs. OAT, °F (°C) | HWST: 180-150/ OAT 20-50  (82-65.6/-6.7-10) | HWST: 180-150/ OAT 20-50  (82-65.6/-6.7-10) | HWST: 180-150/ OAT 20-50  (82-65.6/-6.7-10) | HWST: 180-150/ OAT 20-50  (82-65.6/-6.7-10) |
| Heat loop pumping control | 2-way valves & pump VSD | 2-way valves & pump VSD | 2-way valves & pump VSD | 2-way valves & pump VSD |
| For SI: °C = (°F – 32)/1.8, 1 hp = 0.746 kW, 1 ton = 3.517 kW.  CHW = Chilled Water, ERR = Enthalpy Recovery Ratio, NA = Not Applicable, OSA = Outside Air, PIU = Parallel Powered Induction Unit, RH = Relative Humidity, SP = Static Pressure, Voz = Outdoor airflow to the zone, VSD = Variable Speed Drive. | | | | |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **TABLE C409.6.2.11(2)—TSPR REFERENCE BUILDING DESIGN HVAC SIMPLE SYSTEMS** | | | | | | |
| **BUILDING TYPE PARAMETER** | **BUILDING TYPE** | | | | | |
| **Medium Office (warm)** | **Medium Office (cold)** | **Small Office (warm)** | **Small Office (cold)** | **Retail (warm)** | **Retail (cold)** |
| System type | Package VAV— electric reheat | Package VAV— hydronic reheat | PSZ-HP | PSZ-AC | PSZ-HP | PSZ-AC |
| Fan control | VSD (no SP reset) | VSD (no SP  reset) | Constant volume | Constant volume | Constant volume | Constant volume |
| Main fan power [W/cfm  (W × s/L)] proposed ≥ MERV 13 | 1.285 (2.723) | 1.285 (2.723) | 0.916 (1.941) | 0.916 (1.941) | 0.899 (1.905) | 0.899 (1.905) |
| Main fan power [W/cfm  (W × s/L)] proposed < MERV 13 | 1.176 (2.492) | 1.176 (2.492) | 0.850 (1.808) | 0.850 (1.808) | 0.835 (1.801) | 0.835 (1.801) |
| Zonal fan power [W/cfm (W × s/L)] | 0.35 (0.75) | NA | NA | NA | NA | NA |
| Minimum zone airflow fraction | 30% | 30% | NA | NA | NA | NA |
| Heat/cool sizing factor | 1.25/1.15 | 1.25/1.15 | 1.25/1.15 | 1.25/1.15 | 1.25/1.15 | 1.25/1.15 |
| Supplemental heating availability | NA | NA | < 40°F OAT | NA | < 40°F OAT | NA |
| Outdoor air economizer | No | Yes except 4A | No | Yes except 4A | No | Yes except 4A |
| Occupied OSA source | Packaged unit, occupied damper, all building use types | | | | | |
| Energy recovery ventilator | No | No | No | No | No | No |
| DCV | No | No | No | No | No | No |
| Cooling source | DX, multistage | DX, multistage | DX, 1 stage (heat pump) | DX, single stage | DX, 1 stage (heat pump) | DX, single stage |
| Cooling COP (net of fan) | 3.40 | 3.40 | 3.00 | 3.00 | 3.40 | 3.50 |
| Heating source | Electric resistance | Gas boiler | Heat pump | Furnace | Heat pump | Furnace |
| Heating COP (net of fan)/furnace or boiler efficiency | 1.0 | 75% *Et* | 3.40 | 80% *Et* | 3.40 | 80% *Et* |
| For SI: °C = (°F – 32)/1.8.  NA = Not Applicable, OSA = Outside Air, RH = Relative Humidity, SP = Static Pressure, VSD = Variable Speed Drive. | | | | | | |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **TABLE C409.6.2.11(3)—TSPR REFERENCE BUILDING DESIGN HVAC SIMPLE SYSTEMS** | | | | |
| **BUILDING TYPE PARAMETER** | **BUILDING TYPE** | | | |
| **Hotel (warm)** | **Hotel (cold)** | **Multifamily (warm)** | **Multifamily (cold)** |
| System type | PTHP | PTAC | PTHP | PTAC |
| Fan control | Constant volume | Constant volume | Constant volume | Constant volume |
| Main fan power [W/cfm (W × s/L)] | 0.300 (0.636) | 0.300 (0.636) | 0.300 (0.636) | 0.300 (0.636) |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **TABLE C409.6.2.11(3)—TSPR REFERENCE BUILDING DESIGN HVAC SIMPLE SYSTEMS—continued** | | | | |
| **BUILDING TYPE PARAMETER** | **BUILDING TYPE** | | | |
| **Hotel (warm)** | **Hotel (cold)** | **Multifamily (warm)** | **Multifamily (cold)** |
| Heat/cool sizing factor | 1.25/1.15 | 1.25/1.15 | 1.25/1.15 | 1.25/1.15 |
| Supplemental heating availability | < 40°F | NA | < 40°F | NA |
| Outdoor air economizer | No | No | No | No |
| Occupied OSA source | Packaged unit, occupied damper | Packaged unit, occupied damper | Packaged unit, occupied damper | Packaged unit, occupied damper |
| Energy recovery ventilator | No | No | No | No |
| DCV | No | No | No | No |
| Cooling source | DX, 1 stage (heat pump) | DX, 1 stage | DX, 1 stage (heat pump) | DX, 1 stage |
| Cooling COP (net of fan) | 3.10 | 3.20 | 3.10 | 3.20 |
| Heating source | PTHP | (2) Hydronic boiler | PTHP | (2) Hydronic boiler |
| Heating COP (net of fan)/furnace or boiler efficiency | 3.10 | 75% *Et* | 3.10 | 75% *Et* |
| Heating pump power [W/gpm (W × s/L)] | NA | 19 (300) | NA | 19 (300) |
| Heating coil heating water delta-T, °F (°C) | NA | 50 (27.8) | NA | 50 (27.8) |
| Design HWST, °F (°C) | NA | 180 (82.2) | NA | 180 (82.2) |
| HWST reset setpoint vs. OAT, °F (°C) | NA | HWST: 180-150/ OAT 20-50  (82-65.6/-6.7-10) | NA | HWST: 180-150/ OAT 20-50  (82-65.6/-6.7-10) |
| Heat loop pumping control | NA | 2-way valves & ride pump curve | NA | 2-way valves & ride pump curve |
| For SI: °C = (°F – 32)/1.8.  HWST = Hot Water Supply Temperature, NA = Not Applicable, OAT = Outdoor Air Temperature, OSA = Outside Air. | | | | |

**C409.7 Target design HVAC systems.** Target system descriptions in Tables C409.7(1) through C409.7(3) are provided as reference for Section C403.1.1, Exception 10. The target systems are used for developing mechanical performance factors and do not need to be programmed into TSPR software.

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **TABLE C409.7(1)—TARGET BUILDING DESIGN CRITERIA HVAC COMPLEX SYSTEMS** | | | | |
| **BUILDING TYPE PARAMETER** | **BUILDING TYPE** | | | |
| **Large Office (warm)** | **Large Office (cold)** | **School (warm)** | **School (cold)** |
| System type | VAV/RH | VAV/RH | VAV/RH | VAV/RH |
| Water-cooled chiller | Water-cooled chiller | Water-cooled chiller | Water-cooled chiller |
| Electric reheat (PIU) | Gas boiler | Electric reheat (PIU) | Gas boiler |
| Fan control | VSD (no SP reset) | VSD (no SP reset) | VSD (no SP reset) | VSD (no SP reset) |
| Main fan power [W/cfm (W × s/L] Proposed ≥ MERV 13 | 1.127 (2.388) | 1.127 (2.388) | 1.127 (2.388) | 1.127 (2.388) |
| Zonal fan power [W/CFM (W × s/L)] | 0.35 (0.75) | NA | 0.35 (0.75) | NA |
| Minimum zone airflow fraction | 1.5 × Voz | 1.5 × Voz | 1.2 × Voz | 1.2 × Voz |
| Heat/cool sizing factor | 1.25/1.15 | 1.25/1.15 | 1.25/1.15 | 1.25/1.15 |
| Outdoor air economizer | Yes except 0–1 | Yes | Yes except 0–1 | Yes |
| Occupied OSA (= proposed) | Sum(Voz)/0.75 | Sum(Voz)/0.75 | Sum(Voz)/0.65 | Sum(Voz)/0.65 |
| Energy recovery ventilator efficiency ERR | NA | NA | 50% | 50% |
| ERV bypass SAT setpoint | NA | NA | No bypass | 60°F (15.6°C) except 4A |
| DCV | Yes | Yes | Yes | Yes |
| % Area variable control | 15% | 15% | 70% | 70% |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **TABLE C409.7(1)—TARGET BUILDING DESIGN CRITERIA HVAC COMPLEX SYSTEMS—continued** | | | | |
| **BUILDING TYPE PARAMETER** | **BUILDING TYPE** | | | |
| **Large Office (warm)** | **Large Office (cold)** | **School (warm)** | **School (cold)** |
| % Area on/off control | 65% | 65% | 20% | 20% |
| Cooling source | (2) Water-cooled centrif chillers | (2) Water-cooled centrif chillers | (2) Water-cooled screw chillers | (2) Water-cooled screw chillers |
| Cooling COP (net of fan) | ASHRAE 90.1  Appendix G, Table G3.5.3 | ASHRAE 90.1  Appendix G, Table G3.5.3 | ASHRAE 90.1  Appendix G, Table G3.5.3 | ASHRAE 90.1  Appendix G, Table G3.5.3 |
| Heating source (reheat) | Electric resistance | Gas boiler | Electric resistance | Gas boiler |
| Furnace or boiler efficiency | 1.0 | 90% *Et* | 1.0 | 90% *Et* |
| Condenser heat rejection | Cooling tower | Cooling tower | Cooling tower | Cooling tower |
| Cooling tower efficiency [gpm/hp  (L/s × kW)]—See ASHRAE 90.1 Appendix G, Section G3.1.3.11 | 40.2 (3.40) | 40.2 (3.40) | 40.2 (3.40) | 40.2 (3.40) |
| Tower turndown (> 300 ton (1060 kW)) | 50% | 50% | 50% | 50% |
| Pump (constant flow/variable flow) | Constant flow; 10°F (5.6°C) range | Constant flow; 10°F (5.6°C) range | Constant flow; 10°F (5.6°C) range | Constant flow; 10°F (5.6°C) range |
| Tower approach | ASHRAE 90.1  Appendix G, Table G3.1.3.11 | ASHRAE 90.1  Appendix G, Table G3.1.3.11 | ASHRAE 90.1  Appendix G, Table G3.1.3.11 | ASHRAE 90.1  Appendix G, Table G3.1.3.11 |
| Cooling condenser pump power [W/gpm (W∙s/L)] | 19 (300) | 19 (300) | 19 (300) | 19 (300) |
| Cooling primary pump power [W/gpm (W∙s/L)] | 9 (142) | 9 (142) | 9 (142) | 9 (142) |
| Cooling secondary pump power [W/gpm (W∙s/L)] | 13 (205) | 13 (205) | 13 (205) | 13 (205) |
| Cooling coil chilled water delta-T, °F (°C) | 18 (10) | 18 (10) | 18 (10) | 18 (10) |
| Design chilled water supply temperature,  °F (°C) | 42 (5.56) | 42 (5.56) | 42 (5.56) | 42 (5.56) |
| Chilled water supply temperature (CHWST) reset setpoint vs. OAT, °F (°C) | CHWS 44-54/OAT 80-60 (6.7-12.2)/26.7-15.6) | CHWS 44-54/OAT 80-60 (6.7-12.2)/26.7-15.6) | CHWS 44-54/OAT 80-60 (6.7-12.2)/26.7-15.6) | CHWS 44-54/OAT 80-60 (6.7-12.2)/26.7-15.6) |
| CHW cooling loop pumping control | 2-way valves & pump VSD | 2-way valves & pump VSD | 2-way valves & pump VSD | 2-way valves & pump VSD |
| Heating pump power [W/gpm (W∙s/L)] | 16.1 (254) | 16.1 (254) | 19 (254) | 19 (254) |
| Heating HW delta-T, °F (°C) | 50 (27.78) | 20 (11.11) | 50 (27.78) | 20 (11.11) |
| Design hot water supply temperature (HWST), °F (°C) | 180 (82) | 140 (60) | 180 (82) | 140 (60) |
| Hot water supply temperature (HWST) range vs. outside air temperature (OAT) range | HWST: 180-150/OAT 20-50 (82-65.6/-6.7-10) | HWST: 180-150/OAT 20-50 (82-65.6/-6.7-10) | HWST: 180-150/OAT 20-50 (82-65.6/-6.7-10) | HWST: 180-150/OAT 20-50 (82-65.6/-6.7-10) |
| Heat loop pumping control | 2-way valves & pump VSD | 2-way valves & pump VSD | 2-way valves & pump VSD | 2-way valves & pump VSD |
| For SI: °C = (°F – 32)/1.8.  CHW = Chilled Water, ERR = Enthalpy Recovery Ratio, NA = Not Applicable, OSA = Outside Air, PIU = Parallel Powered Induction Unit, RH = Relative Humidity, SP = Static Pressure, Voz = Outdoor airflow to the zone, VSD = Variable Speed Drive. | | | | |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **TABLE C409.7(2)—TARGET BUILDING DESIGN CRITERIA HVAC SIMPLE SYSTEMS** | | | | | | |
| **BUILDING TYPE PARAMETER** | **BUILDING TYPE** | | | | | |
| **Medium Office(warm)** | **Medium Office (cold)** | **Small Office (warm)** | **Small Office (cold)** | **Retail (warm)** | **Retail (cold)** |
| System type | Package VAV— electric reheat | Package VAV— hydronic reheat | PSZ-HP | PSZ-AC | PSZ-HP | PSZ-AC |
| Fan control | VSD  (with SP reset) | VSD  (with SP reset) | Constant volume | Constant volume | 2-speed | 2-speed |
| Main fan power [W/cfm(  W × s/L)] proposed ≥ MERV 13 | 0.634 (1.343) | 0.634 (1.343) | 0.486 (1.03) | 0.486 (1.03) | 0.585 (1.245) | 0.585 (1.245) |
| Zonal fan power [W/CFM (W × s/L)] | 0.35 (5.53) | NA | NA | NA | NA | NA |
| Minimum zone airflow fraction | 1.5 × Voz | 1.5 × Voz | NA | NA | NA | NA |
| Heat/cool sizing factor | 1.25/1.15 | 1.25/1.15 | 1.25/1.15 | 1.25/1.15 | 1.25/1.15 | 1.25/1.15 |
| Supplemental heating availability | NA | NA | < 40°F  (< 4.4°C) OAT | NA | < 40°F  (< 4.4°C) OAT | NA |
| Outdoor air economizer | Yes except 0–1 | Yes | Yes except 0–1 | Yes | Yes except 0–1 | Yes |
| Occupied OSA source | Packaged unit, occupied damper, all building use types | | | | | |
| Energy recovery ventilator | No | No | No | No | Yes in 0A, 1A, 2A, 3A | Yes all A, 6,7,8 CZ |
| ERR | 50% | 50% |
| DCV | Yes | Yes | No | No | Yes | Yes |
| % Area variable control | 15% | 15% | 80% | 80% |
| % Area on/off control | 65% | 65% | 0% | 0% |
| Cooling source | DX, multistage | DX, multistage | DX, 1 stage (heat pump) | DX, single stage | DX, 2 stage (heat pump) | DX, 2 stage |
| Cooling COP (net of fan) | 3.83 | 3.83 | 3.82 | 3.8248 | 3.765 | 3.765 |
| Heating source | Electric resistance | Gas boiler | Heat pump | Furnace | Heat pump | Furnace |
| Heating COP (net of fan)/ furnace or boiler efficiency | 100% | 81% *Et* | 3.81 | 81% *Et* | 3.536 | 81% *Et* |
| Heating coil HW delta-T, °F (°C) | NA | 20 (11.11) | NA | NA | NA | NA |
| Design HWST, °F (°C) | NA | 140 (60) | NA | NA | NA | NA |
| HWST reset setpoint vs OAT, °F (°C) | NA | HWST: 180-150/OAT 20-50 (82-65.6/-6.7-10) | NA | NA | NA | NA |
| Heat loop pumping control | NA | 2-way valves & ride pump curve | NA | NA | NA | NA |
| Heating pump power [W/gpm (W∙s/L)] | NA | 16.1 | NA | NA | NA | NA |
| For SI: °C = (°F – 32)/1.8.  CHW = Chilled Water, ERR = Enthalpy Recovery Ratio, HWST = Hot Water Supply Temperature, NA = Not Applicable, OAT = Outside Air Temperature, OSA = Outside Air, SP = Static Pressure, Voz = Outdoor airflow to the zone, VSD = Variable Speed Drive. | | | | | | |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **TABLE C409.7(3)—TARGET BUILDING DESIGN CRITERIA HVAC SIMPLE SYSTEMS** | | | | |
| **BUILDING TYPE PARAMETER** | **BUILDING TYPE** | | | |
| **Hotel (warm)** | **Hotel (cold)** | **Multifamily (warm)** | **Multifamily (cold)** |
| System type | PTHP | PTAC with hydronic boiler | Split HP | Split AC |
| Fan control | Cycling | Cycling | Cycling | Cycling |
| Main fan power [W/cfm (W × s/L)] | 0.300 (0.638) | 0.300 (0.638) | 0.246 (0.523) | 0.271 (0.576) |
| Heat/cool sizing factor | 1.25/1.15 | 1.25/1.15 | 1.25/1.15 | 1.25/1.15 |
| Supplemental heating availability | < 40°F (< 4.4°C) | NA | < 40°F (< 4.4°C) | NA |
| Outdoor air economizer | Only CZ 2, 3 | No | No | No |
| Occupied OSA source | DOAS | DOAS | DOAS | DOAS except 3C |
| Energy recovery ventilator | NA | NA | Yes | Yes except 3C |
| ERR | NA | NA | 60% | 60% |
| DCV | Yes | Yes | No | No |
| % Area variable control | 70% | 70% |
| % Area variable control | 0% | 0% |
| Cooling source | DX, 1 stage (heat pump) | DX, 1 stage | DX, 1 stage (heat pump) | DX, 1 stage |
| Cooling COP (net of fan) | 3.83 | 3.83 | 3.823 | 3.6504 |
| Heating source | Heat pump | (2) Hydronic boiler | Heat pump | Furnace |
| Heating COP (net of fan)/furnace or boiler efficiency | 3.44 | 81% *Et* | 3.86 | 80% AFUE |
| Heating pump power (W/gpm (W∙s/L)) | NA | 16.1 | NA | NA |
| Heating coil heating water delta-T, °F (°C) | NA | 20 (11.11) | NA | NA |
| Design HWST, °F (°C) | NA | 140 (60) | NA | NA |
| HWST reset setpoint vs. OAT, °F (°C) | NA | HWST: 180-150/ OAT 20-50  (82-65.6/ -6.7-10) | NA | NA |
| Heat loop pumping control | NA | 2-way valves & ride pump curve | NA | NA |
| For SI: °C = (°F – 32)/1.8.  DOAS = Dedicated Outdoor Air System, ERR = Enthalpy Recovery Ratio, HWST = Hot Water Supply Temperature, NA = Not Applicable, OAT = Outdoor Air Temperature, OSA = Outside Air. | | | | |

### EXISTING BUILDINGS



CHAPTER

**5** [CE]

**User notes:**

***About this chapter:*** *Many buildings are renovated or altered in numerous ways that could affect the energy use of the building as a whole. Chapter 5 requires the application of certain parts of Chapter 4 in order to maintain, if not improve, the conservation of energy by the renovated or altered building.*

SECTION C501—GENERAL

**C501.1 Scope.** The provisions of this chapter shall control the *alteration*, *repair*, *addition* and *change of occupancy* of existing build- ings and structures.

**C501.1.1 Existing buildings.** Except as specified in this chapter, this code shall not be used to require the removal, *alteration* or abandonment of, nor prevent the continued use and maintenance of, an existing building or building system lawfully in existence at the time of adoption of this code.

**C501.2 Compliance.** *Additions*, *alterations*, *repairs*, and changes of occupancy to, or relocation of, existing *buildings* and structures shall comply with Sections C502, C503, C504 and C505 of this code, as applicable, and with the provisions for *alterations*, *repairs*, *additions* and changes of occupancy or relocation, respectively, in the *International Building Code*, *International Existing Building Code, International Fire Code, International Fuel Gas Code, International Mechanical Code, International Plumbing Code, International Property Maintenance Code, International Private Sewage Disposal Code* and NFPA 70. Changes where unconditioned space is changed to conditioned space shall comply with Section C502.

**Exception:** *Additions*, *alterations*, *repairs* or changes of occupancy complying with ANSI/ASHRAE/IES 90.1.

**C501.3 Maintenance.** *Buildings* and structures, and parts thereof, shall be maintained in a safe and sanitary condition. Devices and systems required by this code shall be maintained in conformance to the code edition under which they were installed. The *owner* or the owner’s authorized agent shall be responsible for the maintenance of buildings and structures. The requirements of this chapter shall not provide the basis for removal or abrogation of energy conservation, fire protection and safety systems and devices in exist- ing structures.

**C501.4 New and replacement materials.** Except as otherwise required or permitted by this code, materials permitted by the appli- cable code for new construction shall be used. Like materials shall be permitted for *repairs*, provided that hazards to life, health or property are not created. Hazardous materials shall not be used where the code for new construction would not allow use of these materials in buildings of similar occupancy, purpose and location.

**C501.5 Historic buildings.** Provisions of this code relating to the construction, *repair, alteration*, restoration and movement of struc- tures, and *change of occupancy* shall not be mandatory for *historic buildings* provided that a report has been submitted to the *code official* and signed by a *registered design professional*, or a representative of the State Historic Preservation Office or the historic pres- ervation authority having jurisdiction, demonstrating that compliance with that provision would threaten, degrade or destroy the historic form, fabric or function of the *building*.

SECTION C502—ADDITIONS

**C502.1 General.** *Additions* to an existing building, building system or portion thereof shall conform to the provi- sions of this code as those provisions relate to new construction without requiring the unaltered portion of the existing building or building system to comply with this code. *Additions* shall not create an unsafe or hazardous condition or overload existing building systems. An *addition* shall be deemed to comply with this code if the *addi- tion* alone complies or if the existing building and *addition* comply with this code as a single *building*.

**C502.2 Change in space conditioning.** Any nonconditioned or low-energy space that is altered to become *conditioned space* shall be required to comly with Section C502.

Exceptions:

1. Where the component performance alternative in Section C402.1.4 is used to comply with this section, the proposed UA shall be not greater than 110 percent of the target UA.
2. Where the simulated building performance option in Section C407 is used to comply with this section, the annual *energy cost* of the *proposed design* shall be not greater than 110 percent of the annual *energy cost* otherwise permitted by Section C407.2.

**C502.3 Compliance.** *Additions* shall comply with Sections C502.3.1 through C502.3.8.

**C502.3.1 Vertical fenestration area.** Additions shall comply with the following:

1. Where an addition has a new vertical fenestration area that results in a total building fenestration area less than or equal to that permitted by Section C402.5.1, the addition shall comply with Section C402.1.4, C402.5.3 or C407.
2. Where an addition with vertical fenestration that results in a total building fenestration area greater than Section C402.5.1 or an addition that exceeds the fenestration area greater than that permitted by Section C402.5.1, the fenestra- tion shall comply with Section C402.5.1.1 for the addition only.
3. Where an addition has vertical fenestration that results in a total building vertical fenestration area exceeding that permitted by Section C402.5.1.1, the addition shall comply with Section C402.1.4 or C407.

**C502.3.2 Skylight area.** Skylights shall comply with the following:

1. Where an *addition* has new skylight area that results in a total building fenestration area less than or equal to that permitted by Section C402.5.1, the *addition* shall comply with Section C402.1.4 or C407.
2. Where an *addition* has new skylight area that results in a total building skylight area greater than permitted by Section C402.5.1 or where *additions* have skylight area greater than that permitted by Section C402.5.1, the skylight area shall comply with Section C402.5.1.2 for the *addition* only.
3. Where an *addition* has skylight area that results in a total building skylight area exceeding that permitted by Section C402.5.1.2, the *addition* shall comply with Section C402.1.4 or C407.

**C502.3.3 Building mechanical systems.** New mechanical systems and equipment that are part of the *addition* and serve the building heating, cooling and *ventilation* needs shall comply with Sections C403 and C408.

**C502.3.4 Service water-heating systems.** New service water-heating equipment, controls and service water-heating piping shall comply with Section C404.

**C502.3.5 Pools and inground permanently installed spas.** New pools and inground permanently installed spas shall comply with Section C404.8.

**C502.3.6 Lighting power and systems.** New lighting systems that are installed as part of the *addition* shall comply with Sections C405 and C408.

**C502.3.6.1 Interior lighting power.** The total interior lighting power for the *addition* shall comply with Section C405.3.2 for the *addition* alone, or the existing building and the *addition* shall comply as a single *building*.

**C502.3.6.2 Exterior lighting power.** The total exterior lighting power for the *addition* shall comply with Section C405.5.2 for the *addition* alone, or the existing building and the *addition* shall comply as a single *building*.

**C502.3.7 Additional energy efficiency credit requirements.** *Additions* shall comply with sufficient measures from Sections C406.2 and C406.3 to achieve not less than 50 percent of the number of required efficiency credits from Table C406.1.1(1) based on building occupancy group and *climate zone*. Where a project contains multiple occupancies, credits from Table C406.1.1(1) for each building occupancy shall be weighted by the gross floor area to determine the project weighted average energy credits required. Accessory occupancies shall be included with the primary occupancy group for purposes of this section. *Alterations* to the existing building that are not part of the *addition*, but are permitted with an *addition*, shall be permitted to be used to achieve the required credits.

Exceptions:

* 1. Buildings in Group U (Utility and Miscellaneous), Group S (Storage), Group F (Factory), Group H (High-Hazard).
  2. *Additions* less than 1,000 square feet (93 m2) and less than 50 percent of existing floor area.
  3. *Additions* that do not include the *addition* or replacement of equipment covered by Tables C403.3.2(1) through C403.3.2(16) or Section C404.2.
  4. *Additions* that do not increase *conditioned space*.
  5. Where the *addition* alone or the existing building and *addition* together comply with Section C407.

**C502.3.7.1 Additions not served by heat pumps.** The number of efficiency credits required by Section C502.3.7 shall be multiplied by 1.25 for the following:

1. Additions using purchased energy that is not electricity for space heating or service water heating.
2. Additions served by electric storage water heaters that are not heat pumps.
3. Additions served by total heat pump space heating capacity less than the peak space heating load at heating design conditions calculated in accordance with Section C403.1.1.

**Exceptions:** Additions complying with all of the following:

1. The addition’s peak heating load calculated in accordance with Section C403.1.1 is greater than the addition’s peak cooling load calculated in accordance with Section C403.1.1.
2. The addition’s total heat pump space heating capacity serving the addition is not less than 50 percent of the addition’s space heating load at heating design conditions calculated in accordance with Section C403.1.1.
3. Any energy source other than electricity or onsite renewable energy is used for space heating serving the addition only where a heat pump cannot provide the necessary heating energy to satisfy the thermostat setting.
4. Electric resistance heat serving the addition is used only in accordance with Section C403.4.1.1.

**C502.3.8 Renewable energy systems.** *Additions* shall comply with Section C405.15 for the *addition* alone.

SECTION C503—ALTERATIONS

**C503.1 General.** *Alterations* to any *building* or structure shall comply with the requirements of Section C503. *Alterations* shall be such that the existing building or structure is not less conforming to the provisions of this code than the existing *building* or structure was prior to the *alteration*. *Alterations* to an existing *building*, *building* system or portion thereof shall conform to the provisions of this code as those provisions relate to new construction without requiring the unaltered portions of the existing *building* or *building* system to comply with this code. *Alterations* shall not create an unsafe or hazardous condition or overload existing building systems.

**Exception:** The following *alterations* need not comply with the requirements for new construction, provided that the energy use of the *building* is not increased:

* + 1. Storm windows installed over existing *fenestration*.
    2. Surface-applied window film installed on existing single-pane fenestration assemblies reducing solar heat gain, provided that the code does not require the glazing or *fenestration* to be replaced.
    3. *Roof recover*.
    4. *Roof replacement* where roof assembly insulation is integral to or located below the structural roof deck.
    5. *Air barriers* shall not be required for *roof recover* and *roof replacement* where the *alterations* or renovations to the *building* do not include *alterations*, renovations or *repairs* to the remainder of the *building thermal envelope*.
    6. An existing building undergoing *alterations* that complies with Section C407.

**C503.2 Building thermal envelope.** *Alterations* of existing *building thermal envelope* assemblies shall comply with this section. New *building thermal envelope* assemblies that are part of the *alteration* shall comply with Section C402. An area-weighted average *U- factor* for new and altered portions of the *building thermal envelope* shall be permitted to satisfy the *U-factor* requirements in Table C402.1.4. The existing *R-value* of insulation shall not be reduced or the *U-factor* of a *building thermal envelope* assembly be increased as part of a *building thermal envelope alteration* except where complying with Section C407.

**Exception:** Where the existing *building* exceeds the fenestration area limitations of Section C402.5.1 prior to alteration, the build- ing is exempt from Section C402.5.1 provided that there is no increase in fenestration area.

**C503.2.1 Roof, ceiling and attic alterations.** Insulation complying with Sections C402.1 and C402.2.1, or an *approved* design that minimizes deviation from the insulation requirements, shall be provided for the following *alterations*:

1. An *alteration* of roof/ceiling construction other than *reroofing* where existing insulation located below the roof deck or on an attic floor above *conditioned space* does not comply with Table C402.1.2.
2. Roof replacement or a roof *alteration* that includes removing and replacing the roof covering, where the roof assembly includes insulation entirely above the roof deck.

**Exceptions:** Where compliance with Section C402.1 cannot be met due to limiting conditions on an existing roof, an

*approved* design shall be submitted with the following:

* 1. *Construction documents* that include a report by a *registered design professional* or an *approved source* docu- menting details of the limiting conditions affecting compliance with the insulation requirements.
  2. *Construction documents* that include a roof design by a *registered design professional* or an *approved source*

that minimizes deviation from the insulation requirements.

* 1. Conversion of unconditioned attic space into *conditioned space*.
  2. Replacement of ceiling finishes exposing cavities or surfaces of the roof/ceiling construction.

**C503.2.2 Vertical fenestration.** The addition of *vertical fenestration* that results in a total building *fenestration* area less than or equal to that specified in Section C402.5.1 shall comply with Section C402.1.4, C402.5.3 or C407. The addition of *vertical* fenestra- tion that results in a total building *fenestration* area greater than Section C402.5.1 shall comply with Section C402.5.1.1 for the space adjacent to the new fenestration only. *Alterations* that result in a total building *vertical fenestration* area exceeding that specified in Section C402.5.1.1 shall comply with Section C402.1.4 or C407. Provided that the vertical fenestration area is not changed, using the same vertical fenestration area in the *standard reference design* as the *building* prior to *alteration* shall be an alternative to using the vertical fenestration area specified in Table C407.4.1(1).

**C503.2.2.1 Application to replacement fenestration products.** Where some or all of an existing *fenestration* unit is replaced with a new fenestration product, including sash and glazing, the replacement fenestration unit shall meet the applicable requirements for *U-factor* and *SHGC* in Table C402.5.

**Exception:** An area-weighted average of the *U-factor* of replacement fenestration products being installed in the *building* for each fenestration product category listed in Table C402.5 shall be permitted to satisfy the *U-factor* requirements for each fenestration product category listed in Table C402.5. Individual fenestration products from different product categories listed in Table C402.5 shall not be combined in calculating the area-weighted average *U-factor*.

**C503.2.3 Skylight area.** New *skylight* area that results in a total building *skylight* area less than or equal to that specified in Section C402.5.1 shall comply with Section C402.1.4, C402.5 or C407. The addition of *skylight* area that results in a total building skylight area greater than Section C402.5.1 shall comply with Section C402.5.1.2 for the space adjacent to the new skylights. *Alter- ations* that result in a total building skylight area exceeding that specified in Section C402.5.1.2 shall comply with Section C402.1.4 or C407. Provided that the skylight area is not changed, using the same skylight area in the *standard reference design* as the *build- ing* prior to *alteration* shall be an alternative to using the skylight area specified in Table C407.4.1(1).

**C503.2.4 Above-grade wall alterations.** *Above-grade wall alterations* shall comply with the following:

1. Where wall cavities are exposed, the cavity shall be filled with *cavity insulation* complying with Section C303.1.4. New cavities created shall be insulated in accordance with Section C402.1 or an *approved* design that minimizes deviation from the insulation requirements.
2. Where exterior wall coverings and *fenestration* are added or replaced for the full extent of any exterior wall assembly on one or more elevations of the *building*, insulation shall be provided where required in accordance with one of the following:
   1. An *R-value* of *continuous insulation* not less than that designated in Table C402.1.3 for the applicable *above- grade wall* type and existing cavity insulation *R-value*, if any;
   2. An *R-value* of not less than that required to bring the *above-grade wall* into compliance with Table C402.1.2; or,
   3. An *approved* design that minimizes deviation from the insulation requirements of Section C402.1.
3. Where Items 1 and 2 apply, the insulation shall be provided in accordance with Section C402.1.

Where any of the above requirements are applicable, the *above-grade wall alteration* shall comply with Sections 1402.2 and 1404.3 of the *International Building Code*.

**C503.2.5 Floor alterations.** Where an *alteration* to a floor or floor overhang exposes cavities or surfaces to which insulation can be applied, and the floor or floor overhang is part of the *building thermal envelope*, the floor or floor overhang shall be brought into compliance with Section C402.1 or an *approved* design that minimizes deviation from the insulation requirements. This requirement applies to floor *alterations* where the floor cavities or surfaces are exposed and unobstructed prior to construction.

**C503.2.6 Below-grade wall alterations.** Where unconditioned below-grade space is changed to *conditioned space*, walls enclos- ing such *conditioned space* shall be insulated where required in accordance with Section C402.1. Where the below-grade space is *conditioned space* and where walls enclosing such space are altered, they shall be insulated where required in accordance with Section C402.1.

**C503.2.7 Air barrier.** Altered *building thermal envelope* assemblies shall be provided with an *air barrier* in accordance with Section C402.6.1. Such *air barrier* need not be continuous with unaltered portions of the *building thermal envelope*. Testing requirements of Section C402.6.1.2 shall not be required.

**C503.3 Heating and cooling systems.** New heating, cooling and *duct systems* that are part of the *alteration* shall comply with Section C403.

**C503.3.1 Economizers.** New cooling systems that are part of *alteration* shall comply with Section C403.5.

**C503.3.2 Mechanical system acceptance testing.** Where an *alteration* requires compliance with Section C403 or any of its subsections, mechanical systems that serve the *alteration* shall comply with Sections C408.2.2, C408.2.3 and C408.2.5.

Exceptions:

1. *Buildings* with less than 10,000 square feet (929 m2) and a combined heating, cooling and service water-heating capacity of less than 960,000 Btu/h (281 kW).
2. Systems included in Section C403.5 that serve individual *dwelling units* and *sleeping units*.

**C503.3.3 Duct testing.** *Ducts* and plenums designed to operate at static pressures not less than 3 inches water gauge (747 Pa) that serve an *alteration* shall be tested in accordance with this section where the *alteration* includes any of the following:

1. Twenty-five percent or more of the total length of the ducts in the system are relocated.
2. The total length of all ducts in the system is increased by 25 percent or more.

*Ducts* and plenums shall be leak tested in accordance with the SMACNA *HVAC Air Duct Leakage Test Manual* and shown to have a rate of *air leakage* (CL) less than or equal to 12.0 as determined in accordance with Equation 4-7 of Section C403.13.2.3. Docu- mentation shall be available demonstrating that representative sections totaling not less than 25 percent of the *duct* area have been tested and that all tested sections comply with the requirements of this section.

**C503.3.4 Controls.** New heating and cooling equipment that is part of the *alteration* shall be provided with controls that comply with the control requirements in Sections C403.4 and C403.5 other than the requirements of Sections C403.4.3.3 and C403.4.4.

Exceptions:

* 1. Systems with *direct digital control* of individual *zones* reporting to a central control panel.
  2. The replacement of individual components of multiple-zone VAV systems.

**C503.3.5 System sizing.** New heating and cooling equipment that is part of an *alteration* shall be sized in accordance with Section C403.3.1 based on the existing building features as modified by the *alteration*.

Exceptions:

1. Where it has been demonstrated to the *code official* that compliance with this section would result in heating or cool- ing equipment that is incompatible with the rest of the heating or cooling system.
2. Where it has been demonstrated to the *code official* that the additional capacity will be needed in the future.

**C503.3.6 Replacement or added roof-mounted mechanical equipment.** For roofs with insulation entirely above the roof deck and where existing roof-mounted mechanical equipment is replaced or new equipment is added, and the existing roof does not comply with the insulation requirements for new construction in accordance with Sections C402.1 and C402.2.1, curbs for added or replaced equipment shall be of a height necessary to accommodate the future addition of above-deck roof insulation to be installed in accordance with Section C503.2.1, Item 2. Alternatively, the curb height shall comply with Table C503.3.6. Curb height shall be the distance measured from the top of the curb to the top of the roof deck.

|  |  |
| --- | --- |
| **TABLE C503.3.6—ROOF-MOUNTED MECHANICAL EQUIPMENT CURB HEIGHTS** | |
| **CLIMATE ZONE** | **CURB HEIGHT, MINIMUM** |
| 0, 1, 2 and 3 | 16 inches |
| 4, 5 and 6 | 17 inches |
| 7 and 8 | 18 inches |
| For SI: 1 inch = 25.4 mm. | |

**C503.4 Service hot water systems.** New service hot water systems that are part of the *alteration* shall comply with Section C404.

**C503.4.1 Service hot water system acceptance testing.** Where an *alteration* requires compliance with Section C404 or any of its subsections, service hot water systems that serve the *alteration* shall comply with Sections C408.2.3 and C408.2.5.

Exceptions:

* 1. *Buildings* with less than 10,000 square feet (929 m2) and a combined heating, cooling and service water-heating capacity of less than 960,000 Btu/h (281 kW).
  2. Systems included in Section C403.5 that serve individual *dwelling units* and *sleeping units*.

**C503.5 Lighting systems.** New lighting systems that are part of the *alteration* shall comply with Sections C503.5.1 and C503.5.2.

**C503.5.1 Interior lighting and controls.** *Alterations* to interior spaces, lighting or controls shall comply with the following:

1. Where an alteration of an interior space includes the addition or relocation of full height partitions, the space shall comply with Sections C405.2, C405.3 and C408.3.
2. Where the lighting within interior spaces is altered, those spaces shall comply with Sections C405.2, C405.3 and C408.3.
3. Where the lighting controls within interior spaces are altered, those spaces shall comply with Sections C405.2 and C408.3.

**Exception:** Compliance with Section C405.2.8 is not required for *alterations*.

**C503.5.2 Exterior lighting and controls.** *Alterations* to exterior lighting and controls shall comply with the following:

1. Where the connected exterior lighting power is increased by more than 400 watts, all exterior lighting, including lighting that is not proposed to be altered, shall comply with Section C405.5.
2. Where the combined power of added and replacement luminaires is more than 400 watts, all lighting that is added or altered shall be controlled in accordance with Sections C405.2 and C408.3.

**Exception:** Individual luminaires less than 50 watts provided they pass functional tests verifying *automatic* shut off where daylight is present.

1. Where portions of exterior lighting controls are added or altered, those portions shall comply with Sections C405.2 and C408.3.

**C503.6 Additional energy efficiency credit requirements for alterations.** *Alterations* that are *substantial improvements* shall comply with measures from Sections ~~C406.2, C406.3 or both to earn the number of required credits specified in Table C406.1.1(1) based on building occupancy group and~~ *~~climate zone~~* C402.5 and C405.18 and meet a site energy use intensity (EUI) by building type in accordance with ASHRAE Standard 100, Table 7-2a. *Replacement cost* shall be determined by a registered design professional or *approved* agency and *approved* by the *code official.* Where a project contains multiple occupancies, site EUI requirements ~~Where a project contains multiple occupancies, credits specified in Table C406.1.1(1) for each building occupancy~~ shall be weighted by the gross *conditioned floor area* to determine the weighted average credits site EUI required. Accessory occupancies, other than Group F or H, shall be included with the primary occupancy group for the purposes of this section.

Exceptions:

1. *Alterations* that do not contain *conditioned space*.
2. Portions of *buildings* devoted to manufacturing or industrial use.
3. *Alterations* to *buildings* where the *building* after the *alteration* complies with Section C407.
4. *Alterations* that are permitted with an *addition* complying with Section C502.3.7.

SECTION C504—REPAIRS

**C504.1 General.** *Buildings* and structures, and parts thereof, shall be repaired in compliance with Section C501.3 and this section. Work on nondamaged components that is necessary for the required *repair* of damaged compo- nents shall be considered to be part of the *repair* and shall not be subject to the requirements for *alterations* in this chapter. Routine maintenance required by Section C501.3, ordinary *repairs* exempt from *permit* and abate- ment of wear due to normal service conditions shall not be subject to the requirements for *repairs* in this section.

Where a *building* was constructed to comply with ANSI/ASHRAE/IES 90.1, *repairs* shall comply with the stan- dard and need not comply with Sections C402, C403, C404 and C405.

**C504.2 Application.** For the purposes of this code, the following shall be considered to be *repairs*:

1. Glass-only replacements in an existing sash and frame.
2. *Roof repairs*.
3. *Air barriers* shall not be required for *roof repair* where the *repairs* to the *building* do not include *alterations*, renovations or

*repairs* to the remainder of the *building thermal envelope*.

1. Replacement of existing doors that separate *conditioned space* from the exterior shall not require the installation of a vesti- bule or revolving door, provided that an existing vestibule that separates a *conditioned space* from the exterior shall not be removed.
2. *Repairs* where only the bulb, the ballast or both within the existing luminaires in a space are replaced, provided that the replacement does not increase the installed interior lighting power.

SECTION C505—CHANGE OF OCCUPANCY OR USE

**C505.1 General.** Spaces undergoing a change in occupancy from Group F, H, S or U occupancy classification shall comply with Section C503. *Buildings* or portions of *buildings* undergoing a *change of occupancy* without *alterations* shall comply with Section C505.2.

**Exception:** Where the simulated building performance option in Section C407 is used to comply with this section, the annual *energy cost* of the *proposed design* shall be not greater than 110 percent of the annual *energy cost* otherwise permitted by Section C407.3.

**C505.1.1 Alterations and change of occupancy.** *Alterations* made concurrently with any *change of occu- pancy* shall be in accordance with Section C503.

**C505.1.2 Portions of buildings.** Where changes in occupancy and use are made to portions of an existing building, only those portions of the *building* shall be required to comply with Section C505.2.

**C505.1.3 Additional energy efficiency for changes of occupancy.** Where a space is converted from one occupancy type to another occupancy type, it shall comply with Section C406.1.1.1.

**Exceptions:**

1. Alterations complying with Section C503.6.
2. Where no less than 50 percent of the peak space heating and peak water-heating load of the building is served by heat pump equipment.

**C505.2 Energy use intensities.** *Building thermal envelope*, space heating, cooling, *ventilation*, lighting and *service water heating*

shall comply with Sections C505.2.1 through C505.2.4.

Exceptions:

1. Where it is demonstrated by analysis *approved* by the *code official* that the change will not increase *energy use intensity*.
2. Where the occupancy or use change is less than 5,000 square feet (465 m2) in area.

**C505.2.1 Building thermal envelope.** Where a *change of occupancy* or use is made to a whole *building* that results in a fenestra- tion area greater than the maximum fenestration area allowed by Section C402.5.1, the *building* shall comply with Section C402.1.4, with a proposed UA that shall be not greater than 110 percent of the target UA.

**Exception:** Where the *change of occupancy* or use is made to a portion of the *building*, the new occupancy is exempt from Section C402.5.1, provided that there is not an increase in fenestration area.

**C505.2.2 Building mechanical systems.** Where a *change of occupancy* or use results in the same or increased *energy use intensity*

rank as specified in Table C505.2.2, the systems serving the *building* or space undergoing the change shall comply with Section C403.

|  |  |
| --- | --- |
| **TABLE C505.2.2—BUILDING MECHANICAL SYSTEMS** | |
| **ENERGY USE INTENSITY RANK** | ***INTERNATIONAL BUILDING CODE* OCCUPANCY CLASSIFICATION AND USE** |
| High | A-2, B (laboratories), I-2 |
| Medium | A-1, A-3,a A-4, A-5, B,b E, I-1, I-3, I-4, M, R-4 |
| Low | A-3 (places of religious worship), R-1, R-2, R-3,c S-1, S-2 |
| 1. Excluding places of religious worship. 2. Excluding laboratories. 3. Buildings three stories or less in height above grade plane shall comply with Section R505. | |

**C505.2.3 Service water heating.** Where a *change of occupancy* or use results in the same or increased *energy use intensity* rank as specified in Table C505.2.3, the *service water heating* systems serving the *building* or space undergoing the change shall comply with Section C404.

|  |  |
| --- | --- |
| **TABLE C505.2.3—SERVICE WATER HEATING** | |
| **ENERGY USE INTENSITY RANK** | ***INTERNATIONAL BUILDING CODE* OCCUPANCY CLASSIFICATION AND USE** |
| High | A-2, I-1, I-2, R-1 |
| Low | All other occupancies and uses |

**C505.2.4 Lighting.** Where a *change of occupancy* or use results in the same or increased *energy use intensity* rank as specified in Table C505.2.4, the lighting systems serving the *building* or space undergoing the change shall comply with Section C405 except for Sections C405.2.6 and C405.4.

|  |  |
| --- | --- |
| **TABLE C505.2.4—LIGHTING** | |
| **ENERGY USE INTENSITY RANK** | ***INTERNATIONAL BUILDING CODE* OCCUPANCY CLASSIFICATION AND USE** |
| High | B (laboratories), B (outpatient healthcare), I-2, M |
| Medium | A-2, A-3 (courtrooms), B,a I-1, I-3, I-4, R-1, R-2, R-3,b R-4, S-1, S-2 |
| Low | A-1, A-3,c A-4, E |
| 1. Excluding laboratories and outpatient healthcare. 2. Buildings three stories or less in height above grade plane shall comply with Section R505. 3. Excluding courtrooms. | |

### REFERENCED STANDARDS



CHAPTER

**6** [CE]

**User notes:**

***About this chapter:*** *Chapter 6 lists the full title, edition year and address of the promulgator for all standards that are referenced in the code. The section numbers in which the standards are referenced are also listed.*

*This chapter lists the standards that are referenced in various sections of this document. The standards are listed herein by the promulgating agency of the standard, the standard identification, the effective date and title, and the section or sections of this document that reference the standard. The application of the referenced standards shall be as specified in Section C110.*

**AERC** *Attachments Energy Rating Council, 355 Lexington Ave 15th Floor, New York, NY 10017*

**AERC 1—2017: Procedures for Determining Energy Performance Properties of Fenestration Attachments**

C406.3.4

**AHAM** *Association of Home Appliance Manufacturers, 1111 19th Street NW, Suite 402, Washington, DC 20036*

**ANSI/AHAM RAC-1—2020: Room Air Conditioners**

Table C403.3.2(4)

**AHRI** *Air-Conditioning, Heating, & Refrigeration Institute, 2311 Wilson Blvd, Suite 400, Arlington, VA 22201*

**210/240—2023 (2020): Performance Rating of Unitary Air-conditioning and Air-source Heat Pump Equipment**

Table C403.3.2(1), Table C403.3.2(2), Table C403.3.2(8), Table C403.3.2(9)

**310/380—2017 (CSA-C744-17): Packaged Terminal Air Conditioners and Heat Pumps**

Table C403.3.2(4)

**340/360—2022: Performance Rating of Commercial and Industrial Unitary Air-conditioning and Heat Pump Equipment**

Table C403.3.2(1), Table C403.3.2(2)

**365 (I-P)—2009: Commercial and Industrial Unitary Air-conditioning Condensing Units**

Table C403.3.2(1)

**390 (I-P)—2003: Performance Rating of Single Package Vertical Air-conditioners and Heat Pumps**

Table C403.3.2(4)

**400 (I-P)—2015: Performance Rating of Liquid to Liquid Heat Exchangers**

C403.3.2

**440 (I-P)—2019: Performance Rating of Fan Coils**

C403.13.3

**460—2005: Performance Rating of Remote Mechanical-draft Air-cooled Refrigerant Condensers**

Table C403.3.2(7)

**550/590 (I-P)—2022: Performance Rating of Water-chilling and Heat Pump Water-heating Packages Using the Vapor Compression Cycle**

Table C403.3.2(3), Table C403.3.2(15)

**560—2000: Absorption Water Chilling and Water Heating Packages**

Table C403.3.2(3), Table C403.3.2(15)

**840 (I-P)—1998: Performance Rating of Unit Ventilators**

C403.13.3

**910 (I-P)—2014: Performance Rating of Indoor Pool Dehumidifiers**

Table C403.3.2(11)

**920 (I-P)—2020: Performance Rating of Direct Expansion-Dedicated Outdoor Air System Units (with Addendum 1)**

Table C403.3.2(12), Table C403.3.2(13)

**1200 (I-P)—2022: Performance Rating of Commercial Refrigerated Display Merchandisers and Storage Cabinets**

Table C403.12.1

**1230—2021: Performance Rating of Variable Refrigerant Flow (VRF) Multi-split Air-Conditioning and Heat Pump Equipment**

Table C403.3.2(8), Table C403.3.2(9)

**1250 (I-P)—2020: Standard for Performance Rating in Walk-in Coolers and Freezers**

Table C403.12.2.1(3)

**1360 (I-P)—2017: Performance Rating of Computer and Data Processing Room Air Conditioners**

Table C403.3.2(10), Table C403.3.2(16)

**1380 (I-P)—2019: Demand Response through Variable Capacity HVAC Systems in Residential and Small Commercial Applications**

C406.3

**ANSI/AHRI 1300—2013 (R2023) (I-P): Performance Rating of Commercial Heat Pump Water Heaters**

C406.2.3.1.2

**ASHRAE/ANSI/AHRI/ISO 13256-1—1998 (R2012): Water-to-Air and Brine-to-Air Heat Pumps—Testing and Rating for Performance**

Table C403.3.2(14)

**ASHRAE/ANSI/AHRI/ISO 13256-2—1998 (R2012): Water-to-Water and Brine-to-Water Heat Pumps—Testing and Rating for Performance**

Table C403.3.2(14)

**AISI** *American Iron and Steel Institute, 25 Massachusetts Avenue, NW, Suite 800, Washington, DC 20001*

**AISI S250—22: North American Standard for Thermal Transmittance of Building Envelopes with Cold-Formed Steel Framing, with Supplement 1, dated 2022**

C402.1.2.1.6

**AMCA** *Air Movement and Control Association International, 30 West University Drive, Arlington Heights, IL 60004-1806*

**208—18: Calculation of the Fan Energy Index**

C403.8.3, C403.9.1

**500D—18: Laboratory Methods for Testing Dampers for Rating**

C403.7.7

**ANSI/AMCA 220—21: Laboratory Methods of Testing Air Curtain Units for Aerodynamic Performance Rating**

C402.6.6

**ANSI/AMCA 230—22: Laboratory Methods of Testing Air Circulating Fans for Rating and Certification**

C403.9

**ANSI** *American National Standards Institute, 25 West 43rd Street, 4th Floor, New York, NY 10036*

**ANSI Z21.47—2016/CSA 2.3—2021: Gas-Fired Central Furnaces**

Table C403.3.2(5)

**ANSI Z83.8—2016/CSA 2.6—2016: Gas Unit Heater, Gas Packaged Heaters, Gas Utility Heaters and Gas-Fired Duct Furnaces**

Table C403.3.2(5)

**ANSI/CTA-2045-A—2018: Modular Communications Interface for Energy Management**

C406.3

**ANSI/CTA-2045-B—2018: Modular Communications Interface for Energy Management**

C406.3, C406.3.7

**ANSI/NEMA WD 6—2016: Wiring Devices—Dimensional Specifications**

C405.9.2

**APSP** *Pool & Hot Tub Alliance (formerly the Association of Pool and Spa Professionals), 2111 Eisenhower Avenue, Suite 580, Alexandria, VA 22314*

**14—2019: American National Standard for Portable Electric Spa Energy Efficiency**

C404.9

**ASABE** *American Society of Agricultural and Biological Engineers, 2950 Niles Road, St. Joseph, MI 49085*

**S640—July 2017(R2022): Quantities and Units of Electromagnetic Radiation for Plants (Photosynthetic Organisms)**

C202

**ASHRAE** *ASHRAE, 180 Technology Parkway NW, Peachtree Corners, GA 3009*

**55—2020: Thermal Environmental Conditions for Human Occupancy**

Table C407.4.1(1),

**62.1—2019: Ventilation for Acceptable Indoor Air Quality**

C403.6.1, C406.3.3, Table C409.6.1.10.2(1)

**90.1—2022: Energy Standard for Buildings Except Low-rise Residential Buildings**

C101.3, C401.2.2, C402.1.2, Table C402.1.2, C402.1.2.1, C402.1.3, Table C403.3.2(5), Table C403.3.2(15), C406.2, C406.2, C406.2.1.1,

C409.6.1.3.2, C409.6.1.5, C409.6.1.6, Table C409.6.1.10.2(1), Table C409.7(1), C501.2, C501.3

**90.4—2022: Energy Standard for Data Centers**

C403.1.2, C405.9.1, C405.9.2, C406.2.2.3

**140—2020: Method of Test for Evaluating Building Performance Simulation Software (with Addenda A and B)**

C407.5.1.2, C409.5.1

**ANSI/ASHRAE/ACCA Standard 183—2007 (RA2020): Peak Cooling and Heating Load Calculations in Buildings, Except Low-rise Residential Buildings**

C403.1.1

**ANSI/ASHRAE/ASHE Standard 170—2021: Ventilation of Health Care Facilities**

C409.2.1

**ASHRAE Standard 51—16/ANSI/AMCA Standard 210—16: Laboratory Methods of Testing Fans for Certified Aerodynamic Performance Rating**

Table C403.8.5

**ASHRAE—2020: 2020 ASHRAE Handbook—HVAC Systems and Equipment**

C403.1.1

**ISO/AHRI/ASHRAE 13256-1—1998 (R2012): Water-to-Air and Brine-to-Air Heat Pumps—Testing and Rating for Performance**

Table C403.3.2(14)

**ISO/AHRI/ASHRAE 13256-2—1998 (R2012): Water-to-Water and Brine-to-Water Heat Pumps—Testing and Rating for Performance**

Table C403.3.2(14)

**ASME** *American Society of Mechanical Engineers, Two Park Avenue, New York, NY 10016-5990*

**ASME A17.1—2022/CSA B44—: Safety Code for Elevators and Escalators**

C405.10.2

**ASTM** *ASTM International, 100 Barr Harbor Drive, P.O. Box C700, West Conshohocken, PA 19428-2959*

**C90—21: Specification for Load-bearing Concrete Masonry Units**

Table C402.1.3

**C835—06(2020): Standard Test Method for Total Hemispherical Emittance of Surfaces up to 1400°C**

C402.3

**C1363—19: Standard Test Method for Thermal Performance of Building Materials and Envelope Assemblies by Means of a Hot Box Apparatus**

C303.1.4.1, Table C402.1.2, C402.1.2.1, C402.1.2.1.7, Table C402.1.2.1.7, C402.2.7

**C1371—15: Standard Test Method for Determination of Emittance of Materials Near Room Temperature Using Portable Emissometers**

C402.3, Table C402.4

**C1549—16: Standard Test Method for Determination of Solar Reflectance Near Ambient Temperature Using a Portable Solar Reflectometer**

C402.3, Table C402.4

**D1003—21: Standard Test Method for Haze and Luminous Transmittance of Transparent Plastics**

C402.6.2.3.2

**D8052/D8052M—22: Standard Test Method for Quantification of Air Leakage in Low-Sloped Membrane Roof Assemblies**

C402.6.2.3.2

**E283/E283M—19: Standard Test Method for Determining the Rate of Air Leakage Through Exterior Windows, Curtain Walls and Doors Under Specified Pressure Differences Across the Specimen**

C402.6.1.2.1, C402.6.2.3.2, Table C402.6.3

**E408—13(2019): Standard Test Methods for Total Normal Emittance of Surfaces Using Inspection-meter Techniques**

C402.3, Table C402.4

**E779—19: Standard Test Method for Determining Air Leakage Rate by Fan Pressurization**

C402.6.2.1, C402.6.2.2

**E903—20: Standard Test Method Solar Absorptance, Reflectance and Transmittance of Materials Using Integrating Spheres**

C402.3, Table C402.4

**E1186—22: Standard Practices for Air Leakage Site Detection in Building Envelopes and Air Barrier Systems**

C402.6.2

**E1677—19: Standard Specification for Air Barrier (AB) Material or Assemblies for Low-Rise Framed Building Walls**

C402.6.2.3.2

**E1827—22: Standard Test Methods for Determining Airtightness of Building Using an Orifice Blower Door**

C402.6.2.1, C402.6.2.2

**E1918—21: Standard Test Method for Measuring Solar Reflectance of Horizontal or Low-sloped Surfaces in the Field**

Table C402.4

**E1980—11(2019): Standard Practice for Calculating Solar Reflectance Index of Horizontal and Low-sloped Opaque Surfaces**

Table C402.4

**E2178—21a: Standard Test Method for Determining Air Leakage Rate and Calculation of Air Permeance of Building Materials**

C402.6.2.3.1

**E2357—23: Standard Test Method for Determining Air Leakage of Air Barriers Assemblies**

C402.6.2.3.2

**E3158—18: Standard Test Method for Measuring the Air Leakage Rate of a Large or Multizone Building**

C402.6.2.1

**F1281—17(2021): Standard Specification for Cross-linked Polyethylene/Aluminum/Cross-linked Polyethylene (PEX-AL\_PEX) Pressure Pipe**

Table C404.5.2.1

**F1361—21: Standard Test Method for Performance of Open Vat Fryers**

Table C406.2.6.2(1)

**F1484—18: Standard Test Method for Performance of Steam Cookers**

Table C406.2.6.2(2)

**F1495—20: Standard Specification for Combination Oven Electric or Gas Fired**

Table C406.2.6.2(4)

**F1496—13(2019): Standard Test Method for Performance of Convection Ovens**

Table C406.2.6.2(4)

**F1696—20: Standard Test Method for Energy Performance of Stationary-Rack, Door-Type Commercial Dishwashing Machines**

Table C406.2.6.2(3)

**F1920—20: Standard Test Method for Performance of Rack Conveyor Commercial Dishwashing Machines**

Table C406.2.6.2(3)

**F2093—18: Standard Test Method for Performance of Rack Ovens**

Table C406.2.6.2(4)

**F2144—21: Standard Test Method for Performance of Large Open Vat Fryers**

Table C406.2.6.2(1)

**F2861—20: Standard Test Method for Enhanced Performance of Combination Oven in Various Modes**

Table C406.2.6.2(4)

**CRRC** *Cool Roof Rating Council, 2435 North Lombard Street, Portland, OR 97217*

**ANSI/CRRC S100—2021: Standard Test Methods for Determining Radiative Properties of Materials**

Table C402.4, C402.4.1

**CSA** *CSA Group, 8501 East Pleasant Valley Road, Cleveland, OH 44131-551*

**AAMA/WDMA/CSA 101/I.S.2/A440—22: North American Fenestration Standard/Specification for Windows, Doors and Skylights**

Table C402.6.3

**CAN/CSA C439—18: Laboratory Methods of Test for Rating the Performance of Heat/Energy-Recovery Ventilators**

C403.7.4.1

**CSA B55.1—20: Test Method for Measuring Efficiency and Pressure Loss of Drain Water Heat Recovery Units**

C404.7, C406.2.3.6

**CSA B55.2—20: Drain Water Heat Recovery Units**

C404.7

**CTI** *Cooling Technology Institute, P. O. Box 681807, Houston, TX 77268*

**ATC-105—2019: Acceptance Test Code for Water Cooling Towers**

Table C403.3.2(7)

**ATC-105DS—2019: Acceptance Test Code for Dry Fluid Coolers**

Table C403.3.2(7)

**ATC-105S—2021: Acceptance Test Code for Closed Circuit Cooling Towers**

Table C403.3.2(7)

**ATC-106—2011: Acceptance Test for Mechanical Draft Evaporative Vapor Condensers**

Table C403.3.2(7)

**CTI STD-201 RS—2021: Performance Rating of Evaporative Heat Rejection Equipment**

Table C403.3.2(7)

**DASMA** *Door & Access Systems Manufacturers Association, International, 1300 Sumner Avenue, Cleveland, OH 44115-2851*

**ANSI/DASMA 105—2020: Test Method for Thermal Transmittance and Air Infiltration of Garage Doors and Rolling Doors**

C303.1.3, Table C402.6.3

**DOE** *US Department of Energy, c/o Superintendent of Documents, 1000 Independence Avenue SW, Washington, DC 20585*

**10 CFR 50: Domestic Licensing of Production and Utilization Facilities**

C403.17

**10 CFR, Part 430—2015: Energy Conservation Program for Consumer Products: Test Procedures and Certification and Enforcement Requirement for Plumbing Products; and Certification and Enforcement Requirements for Residential Appliances; Final Rule**

Table C403.3.2(1), Table C403.3.2(2), Table C403.3.2(4), Table C403.3.2(5), Table C403.3.2(6), Table C403.3.2(14), C403.15, Table C404.2, C406.2.3.1.2, Table C406.2.3.5

**10 CFR, Part 430, Appendix U: Uniform Test Method for Measuring the Energy Consumption of Ceiling Fans**

C403.8.5, Table C403.9

**10 CFR, Part 431—2015: Energy Efficiency Program for Certain Commercial and Industrial Equipment: Test Procedures and Efficiency Standards; Final Rules**

Table C403.3.2(6), C403.8.4, C403.12, C403.12.1, Table C403.12.1, C403.12.2, Table C403.12.2.1(2), C404.2, Table C404.2, C405.7, Table C405.7, C405.8, Table C405.8(1), Table C405.8(2), Table C405.8(3), Table C405.8(4)

**FGIA** *Fenestration & Glazing Industry Alliance (formerly, American Architectural Manufacturers Association), 1900 E. Golf Road, Suite 1250, Schaumburg, IL 60173-4268*

**AAMA/WDMA/CSA 101/I.S.2/A440—22: North American Fenestration Standard/Specification for Windows, Doors, and Skylights**

Table C402.6.3

**Green-e** *Green-e, c/o Center for Resource Solutions1012 Torney Ave., 2nd Floor, San Francisco, CA 94129*

**Green-e, Version 1.0, July 7, 2017: Green-e Framework for Renewable Energy Certification**

C405.15.4

**ICC** *International Code Council, Inc., 200 Massachusetts Ave, NW, Suite 250, Washington, DC 20001*

**IBC—24: International Building Code®**

C201.3, C202, C303.1.1, C303.1.2, C303.2, C402.1.5, C402.2.7, C402.6.4, C405.2, C405.5.1, C405.15.2.1, C501.2, C501.2, C503.2.4

**ICC 500—20: Standard for the Design and Construction of Storm Shelters**

C402.5.2

**IFC—24: International Fire Code®**

C201.3, C501.2

**IFGC—24: International Fuel Gas Code®**

C201.3, C501.2

**IMC—24: International Mechanical Code®**

C201.3, C402.1.5, C403.2.2, C403.6, C403.6.1, C403.6.6, C403.7.1, C403.7.2, C403.7.4.2, C403.7.5, C403.7.7, C403.8.6.1, C403.13.1,

C403.13.2, C403.13.2.1, C403.13.2.2, C406.2.2.5, C406.3.3, Table C407.4.1(1), C408.2.2.1, C501.2

**IPC—24: International Plumbing Code®**

C201.3, C501.2

**IPMC—24: International Property Maintenance Code®**

C501.2

**IPSDC—24: International Private Sewage Disposal Code®**

C501.2

**IEC** *IEC Regional Centre for North America, IEC International Electrotechnical Commission, 446 Main Street, 16th Floor, Worcester, MA 01608*

**IEC 62746-10-1—2018: Systems interface between customer energy management system and the power management system – Part 10-1: Open automated demand response**

C406.3

**IEEE** *Institute of Electrical and Electronic Engineers, Inc., 3 Park Avenue, 17th Floor, New York, NY 10016-5997*

* 1. **—2012: IEEE Standard for the Testing, Design, Installation, and Maintenance of Electrical Resistance Trace Heating for Commercial Applications**

C404.6.2

**1547—2018a: IEEE Standard for Interconnection and Interoperability of Distributed Energy Resources with Associated Electric Power Systems Interfaces**

C405.16

**IES** Illuminating Engineering Society, 120 Wall Street, 17th Floor, New York, NY 10005-4001

**ANSI/ASHRAE/IES 90.1—2022: Energy Standard for Buildings, Except Low-Rise Residential Buildings**

C101.3, C401.2, C401.2.2, Table C402.1.2, C402.1.2.1, C402.1.3, Table C402.1.3, Table C403.3.2(5), Table C403.3.2(15), C406.2, C406.2.1.1, C409.6.1.3.2, C409.6.1.3.2, C409.6.1.5, C409.6.1.6, Table C409.6.1.10.2(1), Table C409.7(1), C501.2, C501.3

**ANSI/IES RP-2—2020: Recommended Practice: Lighting Retail Spaces**

C406.2.5

**ANSI/IES RP-3—2020: Recommended Practice: Lighting Educational Facilities**

C406.2.5

**ANSI/IES RP-4—2020: Recommended Practice: Lighting Library Spaces**

C406.2.5

**ANSI/IES RP-6—2020: Recommended Practice: Lighting Sports and Recreational Areas**

C406.2.5

**ANSI/IES RP-7—2020: Recommended Practice: Lighting Industrial Facilities**

C406.2.5

**ANSI/IES RP-8—2021: Recommended Practice: Lighting Roadway and Parking Facilities**

C406.2.5

**ANSI/IES RP-9—2020: Recommended Practice: Lighting Hospitality Spaces**

C406.2.5

**ANSI/IES RP-10—2020: Recommended Practice: Lighting Common Applications**

C406.2.5

**ANSI/IES RP-27—2020: Recommended Practice: Photobiological Safety for Lighting Systems**

C406.2.5

**ANSI/IES RP-29—2020: Recommended Practice: Lighting Hospital and Healthcare Facilities**

C406.2.5

**ANSI/IES RP-30—2020: Recommended Practice: Lighting Museums**

C406.2.5

**ANSI/IES RP-41—2020: Recommended Practice: Lighting Theaters and Worship Spaces**

C406.2.5

**ANSI/IES/ALARP-11—2020: Recommended Practice: Lighting for Interior and Exterior Residential Environments**

C406.2.5

**ISO** *International Organization for Standardization, Chemin de Blandonnet 8, CP 401 - 1214 Vernier, Geneva, Switzerland*

**ISO 9050—2003: Glass in Building: Determination of Light Transmittance, Solar Direct Transmittance, Total Solar Energy Transmittance, Ultraviolet Transmittance and Related Glazing Factors**

C402.3

**ISO 25745-2—2015: Energy Performance of Lifts, Escalators and Moving Walks—Part 2: Energy calculation and classification for lifts (elevators)**

C406.2.6.1

**ISO 27327-1—2009: Fans—Air Curtain Units—Laboratory Methods of Testing for Aerodynamic Performance Rating**

C402.6.6

**ISO/AHRI/ASHRAE 13256-1—1998 (R2012): Water-to-Air and Brine-to-Air Heat Pumps—Testing and Rating for Performance**

Table C403.3.2(14)

**ISO/AHRI/ASHRAE 13256-2—1998 (R2012): Water-to-Water and Brine-to-Water Heat Pumps—Testing and Rating for Performance**

Table C403.3.2(14)

**NEMA** *National Electrical Manufacturers Association, 1300 17th Street N #900, Arlington, VA 22209*

**ANSI/NEMA MG1—2021: Motors and Generators**

C202

**OS 4—2016: Requirements for Air-Sealed Boxes for Electrical and Communication Applications**

C402.6.1.2.2.1

**NFPA** *National Fire Protection Association, 1 Batterymarch Park, Quincy, MA 02169-7471*

**70—23: National Electrical Code**

C405.12.1, C501.2

**NFRC** *National Fenestration Rating Council, Inc., 6305 Ivy Lane, Suite 140, Greenbelt, MD 20770*

**100—2023: Procedure for Determining Fenestration Products *U*-factors**

C303.1.3, Table C402.1.2, C402.1.2.1.7, Table C402.1.4, C402.2.1.2, C402.5.1.1

**200—2023: Procedure for Determining Fenestration Product Solar Heat Gain Coefficient and Visible Transmittance at Normal Incidence**

C303.1.3, C402.5.1.1

**203—2023: Procedure for Determining Visible Transmittance of Tubular Daylighting Devices**

C303.1.3

**300—2023: Test Method for Determining the Solar Optical Properties of Glazing Materials and Systems**

C402.3

**400—2023: Procedure for Determining Fenestration Product Air Leakage**

Table C402.6.3

**OpenADR** *OpenADR Alliance, 111 Deerwood Road, Suite 200, San Roman, CA 94583*

**OpenADR 2.0a and 2.0b—2019: Profile Specification Distributed Energy Resources**

C406.3

**RESNET** *Residential Energy Services Network, Inc., P.O. Box 4561, Oceanside, CA 92052-4561*

**ANSI/RESNET/ICC 380—2022: Standard for Testing Airtightness of Building, Dwelling Unit and Sleeping Unit Enclosures; Airtightness of Heating and Cooling Air Distribution Systems, and Airflow of Mechanical Ventilation Systems**

C402.6.2.2

**SMACNA** *Sheet Metal and Air Conditioning Contractors’ National Association, Inc., 4021 Lafayette Center Drive Chantilly, VA 20151-1219*

**ANSI/SMACNA 016, 2nd edition—2012: HVAC Air Duct Leakage Test Manual Second Edition (ANSI/SMACNA 016—2012)**

C403.13.2.3, C503.3.3

**UL** *UL LLC, 333 Pfingsten Road, Northbrook, IL 60062-2096*

**710—2012: Exhaust Hoods for Commercial Cooking Equipment—with Revisions through February 2021**

C403.7.5

**727—2018: Oil-fired Central Furnaces**

Table C403.3.2(5)

**731—1995: Oil-fired Unit Heaters—with Revisions through October 2015**

Table C403.3.2(5)

**1741—2021: Inverters, Converters, Controllers and Interconnection System Equipment for Use with Distributed Energy Resources**

C405.16

**1784—2015: Air Leakage Tests of Door Assemblies—with Revisions through February 2015**

C402.6.4

**US-FTC** *United States-Federal Trade Commission, 600 Pennsylvania Avenue NW, Washington, DC 20580*

**CFR Title 16 (2015): *R*-Value Rule**

C303.1.4

**WDMA** *Window & Door Manufacturers Association, 2001 K Street NW, 3rd Floor North, Washington, DC 20006*

**AAMA/WDMA/CSA 101/I.S.2/A440—22: North American Fenestration Standard/Specification for windows, doors and skylights**

Table C402.6.3

### BOARD OF APPEALS—COMMERCIAL



APPENDIX

**CA**

*The provisions contained in this appendix are not mandatory unless specifically referenced in the adopting ordinance.*

**User notes:**

***About this appendix:*** *Appendix CA provides criteria for Board of Appeals members. Also provided are procedures by which the Board of Appeals should conduct its business.*

SECTION CA101—GENERAL

**CA101.1 Scope.** A board of appeals shall be established within the jurisdiction for the purpose of hearing applications for modifica- tion of the requirements of this code pursuant to the provisions of Section C109. The board shall be established and operated in accordance with this section, and shall be authorized to hear evidence from appellants and the *code official* pertaining to the appli- cation and intent of this code for the purpose of issuing orders pursuant to these provisions.

**CA101.2 Application for appeal.** Any person shall have the right to appeal a decision of the *code official* to the board. An application for appeal shall be based on a claim that the intent of this code or the rules legally adopted hereunder have been incorrectly inter- preted, the provisions of this code do not fully apply or an equally good or better form of construction is proposed. The application shall be filed on a form obtained from the *code official* within 20 days after the notice was served.

**CA101.2.1 Limitation of authority.** The board shall not have authority to waive requirements of this code or interpret the admin- istration of this code.

**CA101.2.2 Stays of enforcement.** Appeals of notice and orders, other than Imminent Danger notices, shall stay the enforcement of the notice and order until the appeal is heard by the board.

**CA101.3 Membership of board.** The board shall consist of five voting members appointed by the chief appointing authority of the jurisdiction. Each member shall serve for **[INSERT NUMBER OF YEARS]** years or until a successor has been appointed. The board member’s terms shall be staggered at intervals, so as to provide continuity. The *code official* shall be an ex officio member of said board but shall not vote on any matter before the board.

**CA101.3.1 Qualifications.** The board shall consist of five individuals, who are qualified by experience and training to pass on matters pertaining to building construction and are not employees of the jurisdiction.

**CA101.3.2 Alternate members.** The chief appointing authority is authorized to appoint two alternate members who shall be called by the board chairperson to hear appeals during the absence or disqualification of a member. Alternate members shall possess the qualifications required for board membership, and shall be appointed for the same term or until a successor has been appointed.

**CA101.3.3 Vacancies.** Vacancies shall be filled for an unexpired term in the same manner in which original appointments are required to be made.

**CA101.3.4 Chairperson.** The board shall annually select one of its members to serve as chairperson.

**CA101.3.5 Secretary.** The chief appointing authority shall designate a qualified clerk to serve as secretary to the board. The secretary shall file a detailed record of all proceedings which shall set forth the reasons for the board’s decision, the vote of each member, the absence of a member and any failure of a member to vote.

**CA101.3.6 Conflict of interest.** A member with any personal, professional or financial interest in a matter before the board shall declare such interest and refrain from participating in discussions, deliberations and voting on such matters.

**CA101.3.7 Compensation of members.** Compensation of members shall be determined by law.

**CA101.3.8 Removal from the board.** A member shall be removed from the board prior to the end of their terms only for cause. Any member with continued absence from regular meeting of the board may be removed at the discretion of the chief appointing authority.

**CA101.4 Rules and procedures.** The board shall establish policies and procedures necessary to carry out its duties consistent with the provisions of this code and applicable state law. The procedures shall not require compliance with strict rules of evidence, but shall mandate that only relevant information be presented.

**CA101.5 Notice of meeting.** The board shall meet upon notice from the chairperson, within 10 days of the filing of an appeal or at stated periodic intervals.

**CA101.5.1 Open hearing.** All hearings before the board shall be open to the public. The appellant, the appellant’s representative, the *code official* and any person whose interests are affected shall be given an opportunity to be heard.

**CA101.5.2 Quorum.** Three members of the board shall constitute a quorum.

**CA101.5.3 Postponed hearing.** When five members are not present to hear an appeal, either the appellant or the appellant’s representative shall have the right to request a postponement of the hearing.

**CA101.6 Legal counsel.** The jurisdiction shall furnish legal counsel to the board to provide members with general legal advice concerning matters before them for consideration. Members shall be represented by legal counsel at the jurisdiction’s expense in all matters arising from service within the scope of their duties.

**CA101.7 Board decision.** The board shall only modify or reverse the decision of the *code official* by a concurring vote of three or more members.

**CA101.7.1 Resolution.** The decision of the board shall be by resolution. Every decision shall be promptly filed in writing in the office of the *code official* within three days and shall be open to the public for inspection. A certified copy shall be furnished to the appellant or the appellant’s representative and to the *code official*.

**CA101.7.2 Administration.** The *code official* shall take immediate action in accordance with the decision of the board.

**CA101.8 Court review.** Any person, whether or not a previous party of the appeal, shall have the right to apply to the appropriate court for a writ of certiorari to correct errors of law. Application for review shall be made in the manner and time required by law following the filing of the decision in the office of the chief administrative officer.

### SOLAR-READY ZONE—COMMERCIAL



APPENDIX

**CB**

*The provisions contained in this appendix are not mandatory unless specifically referenced in the adopting ordinance.*

**User notes:**

***About this appendix:*** *Appendix CB is intended to encourage the installation of renewable energy systems by preparing buildings for the future installation of solar energy equipment, piping and wiring.*

SECTION CB101—SCOPE

**CB101.1 General.** These provisions shall be applicable for new construction where solar-ready provisions are required.

SECTION CB102—GENERAL DEFINITION

**SOLAR-READY ZONE.** A section or sections of the roof or building overhang designated and reserved for the future installation of a solar photovoltaic or solar thermal system.

SECTION CB103—SOLAR-READY ZONE

**CB103.1 General.** A solar-ready zone shall be located on the roof of buildings that are five stories or less in height above grade plane, and are oriented between 110 degrees and 270 degrees of true north or have *low slope* roofs. Solar-ready zones shall comply with Sections CB103.2 through CB103.8.

Exceptions:

* + 1. A *building* with a permanently installed, on-site renewable energy system.
    2. A *building* with a solar-ready zone that is shaded for more than 70 percent of daylight hours annually.
    3. A *building* where the licensed design professional certifies that the incident solar radiation available to the *building* is not suitable for a solar-ready zone.
    4. A *building* where the licensed design professional certifies that the solar zone area required by

Section CB103.3 cannot be met because of extensive rooftop equipment, skylights, *vegetative roof* areas or other obstructions.

**CB103.2 Construction document requirements for a solar-ready zone.** *Construction documents* shall indicate the solar-ready zone.

**CB103.3 Solar-ready zone area.** The total solar-ready zone area shall be not less than 40 percent of the roof area calculated as the horizontally projected gross roof area less the area covered by skylights, occupied roof decks, *vegetative roof* areas and mandatory access or set back areas as required by the *International Fire Code*. The solar-ready zone shall be a single area or smaller, separated sub-zone areas. Each sub-zone shall be not less than 5 feet (1524 mm) in width in the narrowest dimension.

**CB103.4 Obstructions.** Solar ready zones shall be free from obstructions, including pipes, vents, *ducts*, HVAC equipment, skylights and roof-mounted equipment.

**CB103.5 Roof loads and documentation.** A collateral dead load of not less than 5 pounds per square foot (5 psf) (24.41 kg/m2) shall be included in the gravity and lateral design calculations for the solar-ready zone. The structural design loads for roof dead load and roof live load shall be indicated on the *construction documents*.

**CB103.6 Interconnection pathway.** *Construction documents* shall indicate pathways for routing of conduit or piping from the solar- ready zone to the electrical service panel or service hot water system.

**CB103.7 Electrical service reserved space.** The main electrical service panel shall have a reserved space to allow installation of a dual-pole circuit breaker for future solar electric and shall be labeled “For Future Solar Electric.” The reserved space shall be posi- tioned at the end of the panel that is opposite from the panel supply conductor connection.

**CB103.8 Construction documentation certificate.** A permanent certificate, indicating the solar-ready zone and other requirements of this section, shall be posted near the electrical distribution panel, *water heater* or other conspicuous location by the builder or *registered design professional*.

### ZERO ENERGY COMMERCIAL BUILDING PROVISIONS



APPENDIX

**CC**

*The provisions contained in this appendix are not mandatory unless specifically referenced in the adopting ordinance.*

**User notes:**

***About this appendix:*** *Appendix CC provides a model for applying new renewable energy generation when new buildings add electric load to the grid.*

*This renewable energy will avoid the additional emissions that would otherwise occur from conventional power generation.*

SECTION CC101—GENERAL

**CC101.1 Purpose.** The purpose of this appendix is to supplement the *International Energy Conservation Code* and require

renewable energy systems of adequate capacity to achieve net zero operational energy.

**CC101.2 Scope.** This appendix applies to new buildings that are addressed by the *International Energy Conservation Code*.

Exceptions:

1. Detached one- and two-family dwellings and townhouses as well as Group R-2 buildings three stories or less in height above grade plane, manufactured homes (mobile dwellings), and manufactured houses (modular dwellings).
2. Buildings that use neither electricity nor fossil fuel.

SECTION CC102—DEFINITIONS

**CC102.1 Definitions.** The definitions contained in this section supplement or modify the definitions in the *Inter-national Energy Conservation Code*.

**ADJUSTED OFF-SITE RENEWABLE ENERGY.** The amount of energy production from off-site renewable energy systems that may be used to offset building energy.

**BUILDING ENERGY.** All energy consumed at the *building site* as measured at the site boundary. Contributions from on-site or off-site renewable energy systems shall not be considered when determining the building energy.

**DIRECT ACCESS TO WHOLESALE MARKET.** An agreement by the *owner* and a renewable energy developer to purchase renewable energy from the wholesale market.

**DIRECT OWNERSHIP.** An off-site renewable energy system under the ownership or control of the building project

**GREEN RETAIL PRICING.** A program by the retail electricity provider to provide 100 percent renewable energy to the building project

*owner*.

**MINIMUM RENEWABLE ENERGY REQUIREMENT.** The minimum amount of on-site or adjusted off-site renewable energy needed to comply with this appendix.

**OFF-SITE RENEWABLE ENERGY SYSTEM.** A renewable energy system that serves the building project and is not an on-site renewable energy system, including contracted purchases of renewable energy and renewable energy certificates (RECs).

**ON-SITE RENEWABLE ENERGY SYSTEM.** Renewable energy systems located on any of the following:

1. The building.
2. The property on which the building is located.
3. A property that shares a boundary with and is under the same ownership or control as the property on which the building is located.
4. A property that is under the same ownership or control as the property on which the building is located and is separated only by a public right-of-way from the building served by the renewable energy system.

**RENEWABLE ENERGY INVESTMENT FUND (REIF).** A fund established by a jurisdiction to accept payment from building project owners to construct or acquire interests in qualifying renewable energy systems, together with their associated RECS, on the building project owner’s behalf.

**RENEWABLE ENERGY SYSTEM.** Photovoltaic, solar thermal, geothermal energy extracted from hot fluid or steam, wind, or other

*approved* systems used to generate renewable energy.

**SEMIHEATED SPACE.** An *enclosed space* within a *building* that is heated by a heating system whose output capacity is greater than or equal to 3.4 Btu/h × ft2 of floor area but is not a *conditioned space*.

**APPENDIX CC—ZERO ENERGY COMMERCIAL BUILDING PROVISIONS**

SECTION CC103—MINIMUM RENEWABLE ENERGY

**CC103.1 Renewable energy.** On-site renewable energy systems shall be installed, or adjusted off-site renewable energy shall be procured to meet the minimum renewable energy requirement in accordance with Equation CC-1.

**Equation CC-1** *REon-site* + *REoff-site*  *REmin*

where:

*REon-site* = Annual site energy production from on-site renewable energy systems, including installed on- site renewable energy systems used for compliance with Sections C405.13.1 and C406.

*REoff-site* = Adjusted annual site energy production from off-site renewable energy systems that is permit- ted to be credited against the minimum renewable energy requirement. This includes off-site renewable energy purchased for compliance with Section C405.13.2.

*REmin* = Minimum renewable energy requirement.

When Section C401.2.1 is used for compliance with the *International Energy Conservation Code*, the minimum renewable energy requirement shall be determined by multiplying the gross conditioned floor area plus the gross semiheated floor area of the proposed building by the prescriptive renewable energy requirement from Table CC103.1. An area-weighted average shall be used for mixed-use buildings.

When Section C401.2.1, Item 2 or Section C401.2.2 is used for compliance with the *International Energy Conservation Code*, the minimum renewable energy requirement shall be equal to the building energy as determined from energy simulations.

|  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE CC103.1—PRESCRIPTIVE RENEWABLE ENERGY REQUIREMENT FOR BUILDING TYPES AND CLIMATES (kWh/ft2/yr)** | | | | | | | | | | | | |
| **CLIMATE ZONE** | **BUILDING AREA TYPE** | | | | | | | | | | | |
| **Multifamily (R-2)** | **Healthcare/ Hospital**  **(I-2)** | **Hotel/ Motel (R-2)** | **Office (B)** | **Restaurant (A-2)** | **Retail (M)** | **School (E)** | **Warehouse (S)** | **Grocery Store (M)** | **Laboratory (B)** | **Assembly (A)** | **All Others** |
| 0A | 13 | 35 | 23 | 10 | 129 | 17 | 16 | 3 | 27 | 41 | 5 | 17 |
| 0B | 12 | 34 | 22 | 10 | 123 | 17 | 15 | 3 | 26 | 40 | 5 | 16 |
| 1A | 11 | 32 | 20 | 9 | 113 | 14 | 13 | 3 | 24 | 36 | 4 | 15 |
| 1B | 11 | 32 | 20 | 9 | 118 | 15 | 14 | 3 | 24 | 37 | 5 | 15 |
| 2A | 11 | 32 | 20 | 8 | 114 | 13 | 12 | 3 | 22 | 34 | 4 | 14 |
| 2B | 11 | 30 | 18 | 8 | 108 | 12 | 11 | 3 | 22 | 33 | 4 | 13 |
| 3A | 11 | 30 | 18 | 8 | 117 | 13 | 11 | 3 | 21 | 31 | 4 | 13 |
| 3B | 10 | 29 | 18 | 8 | 110 | 12 | 10 | 3 | 20 | 31 | 4 | 13 |
| 3C | 9 | 28 | 18 | 7 | 100 | 10 | 9 | 2 | 18 | 27 | 3 | 12 |
| 4A | 12 | 31 | 18 | 8 | 123 | 15 | 11 | 6 | 21 | 32 | 4 | 14 |
| 4B | 11 | 29 | 18 | 7 | 113 | 12 | 10 | 4 | 20 | 30 | 4 | 13 |
| 4C | 10 | 28 | 17 | 7 | 111 | 13 | 10 | 4 | 18 | 28 | 3 | 13 |
| 5A | 12 | 31 | 19 | 8 | 133 | 17 | 11 | 8 | 22 | 34 | 4 | 15 |
| 5B | 11 | 29 | 18 | 8 | 125 | 14 | 11 | 5 | 21 | 31 | 4 | 14 |
| 5C | 10 | 29 | 17 | 7 | 116 | 13 | 10 | 4 | 18 | 27 | 3 | 13 |
| 6A | 14 | 33 | 20 | 10 | 151 | 20 | 13 | 11 | 26 | 39 | 5 | 17 |
| 6B | 13 | 33 | 19 | 8 | 137 | 17 | 11 | 7 | 22 | 34 | 4 | 16 |
| 7 | 14 | 37 | 21 | 9 | 164 | 20 | 13 | 10 | 25 | 37 | 5 | 18 |
| 8 | 15 | 40 | 22 | 11 | 190 | 23 | 16 | 10 | 28 | 43 | 5 | 20 |
| For SI: 1 kilowatt hour per square foot = 10.76 kWh/m2. | | | | | | | | | | | | |

**CC103.2 Calculation of on-site renewable energy.** The annual energy production from on-site renewable energy systems shall be determined using *approved* software.

|  |  |  |
| --- | --- | --- |
| **TABLE CC103.2—PROCUREMENT FACTORS FOR RENEWABLE ENERGY SYSTEM COMPLIANCE ALTERNATIVES** | | |
| **ON-SITE RENEWABLE ENERGY** | **PROCUREMENT FACTOR** | |
| **Unbundled RECs** | **Other Procurement Methods** |
| 7.5 W/ft2 of roof area or more or where one or more of Exceptions 1, 2 and 3 to Section C405.15.1 are satisfied. | 0.20 | 1.0 |

|  |  |  |
| --- | --- | --- |
| **TABLE CC103.2—PROCUREMENT FACTORS FOR RENEWABLE ENERGY SYSTEM COMPLIANCE ALTERNATIVES—continued** | | |
| **ON-SITE RENEWABLE ENERGY** | **PROCUREMENT FACTOR** | |
| Less than 7.5 W/ft2 of roof area and none among Exceptions 1, 2 and 3 to Section C405.15.1 is satisfied. | 0.20 | 0.75 |
| For SI: 1 watt per square foot = W/0.0929 m2. W = Watts. | | |

**CC103.2.1 Renewable energy certificates.** Renewable energy certificates (RECs) associated with the on-site renewable energy system shall be assigned to the initial and subsequent building owner(s) for a cumulative period of not less than 15 years. The building owner(s) are permitted to transfer RECs to building tenants occupying the *building*.

**CC103.3 Off-site renewable energy.** Off-site energy shall comply with Sections CC103.3.1 and CC103.3.2.

**CC103.3.1 Off-site procurement methods.** One or more of the following off-site renewable energy procurement methods shall be used to comply with Section CC103.1:

* 1. Community renewables energy facility.
  2. *Renewable energy investment fund*.
  3. *Financial renewable energy power purchase agreement*.
  4. *Direct ownership.*
  5. *Direct access to wholesale market.*
  6. Green retail pricing.
  7. Unbundled Renewable Energy Certificates (RECs).
  8. *Physical renewable energy power purchase agreement*.

**CC103.3.2 Requirements for all procurement methods.** Off-site renewable energy systems and procurement methods used to comply with Section CC103.1 shall comply with all of the following:

1. The building *owner* shall sign a legally binding contract or other *approved* agreement to procure qualifying off-site renewable energy.
2. The procurement contract shall have duration of not less than 15 years and shall be structured to survive a partial or full transfer of ownership of the property.
3. RECs associated with the procured *off-site renewable energy* shall comply with the following requirements:
   1. The RECs shall be retained or retired by or on behalf of the property *owner* or tenant for a period of not less than 15 years.
   2. The RECs shall be created within a 12-month period of use of the REC.
   3. The RECs shall be from a generating asset constructed not more than 5 years before the issuance of the certifi- cate of occupancy.
4. The generating source shall be a renewable energy system.
5. The generation source shall be located where the energy can be delivered to the *building site* by any of the following:
   1. Direct connection to the off-site renewable energy facility.
   2. The local utility or distribution entity.
   3. An interconnected electrical network where energy delivery capacity between the generator and the *building*

site is available.

1. Records on power sent to or purchased by the building shall be retained by the building owner and made available for inspection by the code official upon request.

**CC103.3.3 Adjusted off-site renewable energy.** The process for calculating the adjusted *off-site renewable energy* is shown in Equation CC-2.

**Equation CC-2** *REoff-site* = *PFNonRecs* × *RENonRecs* + 0.20 × *RERecs*

where:

*REoff-site* = Adjusted off-site renewable energy.

*PFNonRecs* = The renewable energy procurement factor for off-site renewable energy other than RECs, in accordance with Section CC103.3.3.1.

*RENonRecs* = Annual energy production for renewable energy procurement methods other than RECs.

*RERecs* = Annual energy production associated with unbundled RECs.

**CC103.3.3.1 Procurement factors.** The procurement factors for renewable energy system compliance alternatives shall be as specified in Table CC103.2.

### THE 2030 GLIDE PATH



APPENDIX

**CD**

*The provisions contained in this appendix are not mandatory unless specifically referenced in the adopting ordinance.*

**User notes:**

***About this appendix:*** *This voluntary appendix is suited for adopting authorities that wish to extend beyond the mandatory provisions of this code toward zero net energy goals. Appendix CD is intended to be adopted by jurisdictions that will require new construction to operate at zero net energy by the year 2030. It reduces the net annual energy use of buildings by approximately one-third in comparison with buildings constructed in compliance with the 2021 IECC. It is assumed that the 2027 and 2030 editions will also reduce energy use by one-third each.*

SECTION CD101—COMPLIANCE

CD101.1 Reserved.

**CD101.2 Simulated Building Performance compliance.** Where compliance is demonstrated using the Simulated Building Performance option of Section C401.2.1, the percentage of annual *energy cost* (PAEC), applied to the *standard reference design* referenced in Equation 4-32, shall be multiplied by 0.97.

**CD101.3 On-site renewable electricity systems.** In addition to any renewable energy generation equipment provided to comply with Section C406.3, buildings shall install equipment for *on-site renewable energy* generation with a direct current (DC) nameplate capacity rating of not less than that computed using Equation CD-2.

**Equation CD-1** *AA* = *CA* + *SNA*/3 where:

*AA* = Adjusted area, in ft2 (m2).

*CA* = Conditioned area, in ft2 (m2).

*SNA* = Semi-heated and nonconditioned area, in ft2 (m2).

**Equation CD-2** *REQ* = *AA* × *CF*

where:

*REQ* = Required on-site capacity, in DC watts.

*AA* = Adjusted area from Equation CD-1, in ft2 (m2).

*CF* = Capacity factor from Table CD101.3, in watts/ft2 (m2).

Exceptions:

1. Any required renewable energy generation capacity in excess of 10 watts per square foot (108 W/m2) of net available roof area is permitted to be provided using an off-site renewable energy system in accordance with Section CD101.4. For the purposes of this section, net available roof area is the gross roof area minus the roof area occupied by any combination of skylights, mechanical equipment, vegetated areas, required access path- ways, vehicle parking and occupied roof terrace area.
2. The following buildings are permitted to provide off-site renewable energy generation in accordance with Section CD101.4 in lieu of all or part of the *on-site renewable energy* generation capacity required by Section CD101.3:
   1. Any *building* where more than 50 percent of roof area would be shaded from direct-beam sunlight by existing natural objects or by structures that are not part of the *building* for more than 2,500 annual hours between 8:00 a.m. and 4:00 p.m.
   2. Any *building* with gross *conditioned floor area* less than 1,000 square feet (93 m2).
   3. Any *building* whose primary roof slope is 2 units vertical in 12 units horizontal (17 percent slope) or greater.
3. Alternate forms of renewable energy generation capacity are permitted where the annual energy generation is not less than that produced by the required solar capacity, and where annual energy generation is calculated using an *approved* methodology.
4. All or part of the required renewable energy generation capacity is permitted to be replaced by other efficiency measures provided that such measures will reduce the annual energy consumption of the *building* by an amount no less than that which would otherwise be produced annually by the required renewable energy capacity, as calculated using the Simulated Building Performance compliance path in Section C407 and an *approved* calculation methodology for solar production.

|  |  |
| --- | --- |
| **TABLE CD101.3—ON-SITE RENEWABLE ELECTRICITY** | |
| **CLIMATE ZONE** | **CAPACITY FACTOR** |
| 1A, 2B, 3B, 3C, 4B and 5B | 2.0 W/ft2 |
| 0A, 0B, 1B, 2A, 3A and 6B | 2.3 W/ft2 |
| 4A, 4C, 5A, 5C, 6A, 7 and 8 | 2.6 W/ft2 |
| For SI: 1 watt per square foot = 10.76 W/m2. | |

**CD101.4 Off-site renewable energy.** *Buildings* that qualify for one or more of the exceptions to Section CD101.3 and that do not have on-site renewable energy systems sufficiently sized to fully comply with Section CD101.3 shall procure off-site renewable energy in accordance with Sections CD101.4.1 through CD101.4.3. Such procured energy shall provide not less than the total annual required off-site renewable energy determined in accordance with Equation CD-4 and shall be provided in addition to any renewable energy provided to comply with Section C406.3.

**Equation CD-3** *DEF* = *REQ* - *INSTL*

where:

*DEF* = Renewable capacity deficit, in DC watts.

*REQ* = Required on-site capacity in DC watts, from Equation CD-2.

*INSTL* = Installed on-site capacity, in DC watts.

**Equation CD-4** *OFF* = 4.4 × *DEF*

where:

*OFF* = Off-site renewable energy to be procured, in kWh/year.

**CD101.4.1 Off-site procurement.** The *building owner* shall procure and be credited for the total amount of off-site renewable energy required by Equation CD-4. Procured off-site renewable energy shall comply with the requirements applicable to not less than one of the following:

1. Community renewables energy facility.
2. Financial renewable energy power purchase agreement.
3. Physical renewable energy power purchase agreement.
4. Direct ownership.
5. Renewable Energy Investment Fund.
6. Green retail tariff.

**CD101.4.2 Off-site contract.** The renewable energy shall be delivered or credited to the *building site* under an energy contract with a duration of not less than 10 years. The contract shall be structured to survive a partial or full transfer of ownership of the building property. The total required off-site renewable energy shall be procured in equal installments over the duration of the off-site contract.

**CD101.4.3 Renewable energy certificate (REC) documentation.** The property *owner* or *owner’s* authorized agent shall demon- strate that where RECs are associated with on-site and off-site renewable energy production required by Sections CD101.3 and CD101.4, the following criteria shall be met:

1. The RECs shall be retained and retired by or on behalf of the property *owner* or tenant for a period of not less than 10 years or the duration of the contract in Section CD101.4.2, whichever is less.
2. The RECs shall be created within a 12-month period of the use of the REC.
3. The RECs represent a generating asset constructed not more than 5 years before the issuance of the certificate of occupancy.

### REQUIRED HVAC TOTAL SYSTEM PERFORMANCE RATIO (TSPR)



APPENDIX

**CE**

*The provisions contained in this appendix are not mandatory unless specifically referenced in the adopting ordinance.*

**User notes:**

***About this appendix:*** *Appendix CE can be adopted for stretch codes and utility incentive certification that requires Total System Performance Ratio (TSPR) analysis where it is applicable and requires a higher level of performance, saving 5 percent versus minimum efficiency systems.*

SECTION CE101—GENERAL

**CE101.1 Required HVAC total system performance ratio (TSPR).** For jurisdictions that wish to adopt a stretch code or HVAC incentive system, make the following changes to Section C403.

**CE101.2 (Replace Section C403.1 with the following) General.** Mechanical systems and equipment serving the building heating, cooling, ventilating or refrigerating needs shall comply with one of the following:

* 1. Sections C403.1.1 and C403.2 through C403.17 and where applicable, Section C409.
  2. *Data centers* shall comply with Sections C403.1.1, C403.1.2 and C403.6 through C403.17.

CE101.3 HVAC total system performance ratio (TSPR). (Add the following three exceptions to Section C409.2.)

**Exceptions:**

* + 1. Buildings with *conditioned floor area* less than 5,000 square feet (465 m2).
    2. *Alterations* to existing buildings that do not substantially replace the entire HVAC system and are not serving initial build- out construction.
    3. HVAC systems meeting or exceeding all the requirements of the applicable target design HVAC system described in Tables C409.7(1) through C409.7(3).

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE CE101.3—MECHANICAL PERFORMANCE FACTORS** | | | | | | | | | | | | | | | | | | | | |
| **BUILDING TYPE** | **OCCUPANCY GROUP** | **CLIMATE ZONE** | | | | | | | | | | | | | | | | | | |
| **0A** | **0B** | **1A** | **1B** | **2A** | **2B** | **3A** | **3B** | **3C** | **4A** | **4B** | **4C** | **5A** | **5B** | **5C** | **6A** | **6B** | **7** | **8** |
| Office (small and medium)a | B | 0.68 | 0.68 | 0.67 | 0.67 | 0.65 | 0.62 | 0.67 | 0.65 | 0.61 | 0.76 | 0.67 | 0.74 | 0.80 | 0.73 | 0.76 | 0.82 | 0.79 | 0.83 | 0.85 |
| Office (large)a | B | 0.79 | 0.79 | 0.80 | 0.80 | 0.75 | 0.78 | 0.68 | 0.77 | 0.73 | 0.64 | 0.72 | 0.60 | 0.67 | 0.68 | 0.60 | 0.69 | 0.67 | 0.67 | 0.67 |
| Retail | M | 0.57 | 0.54 | 0.48 | 0.52 | 0.44 | 0.44 | 0.41 | 0.48 | 0.38 | 0.43 | 0.54 | 0.65 | 0.44 | 0.65 | 0.64 | 0.48 | 0.43 | 0.42 | 0.36 |
| Hotel/motel | R-1 | 0.59 | 0.59 | 0.60 | 0.60 | 0.59 | 0.65 | 0.58 | 0.67 | 0.69 | 0.43 | 0.56 | 0.49 | 0.36 | 0.45 | 0.48 | 0.33 | 0.36 | 0.29 | 0.25 |
| Multifamily/ dormitory | R-2 | 0.61 | 0.60 | 0.64 | 0.60 | 0.62 | 0.61 | 0.56 | 0.68 | 0.52 | 0.50 | 0.48 | 0.42 | 0.51 | 0.45 | 0.36 | 0.52 | 0.48 | 0.48 | 0.45 |
| School/ education and libraries | E (A-3) | 0.78 | 0.77 | 0.76 | 0.75 | 0.71 | 0.68 | 0.67 | 0.68 | 0.64 | 0.69 | 0.68 | 0.65 | 0.78 | 0.69 | 0.58 | 0.85 | 0.76 | 0.79 | 0.73 |
| For SI: 1 square foot = 0.0929 m2.  a. Large office = gross conditioned floor area greater than 150,000 square feet or greater than five floors; all other offices are small or medium. | | | | | | | | | | | | | | | | | | | | |

### ENERGY CREDITS



APPENDIX

**CF**

*The provisions contained in this appendix are not mandatory unless specifically referenced in the adopting ordinance.401*

**User notes:**

***About this appendix:*** *Appendix CF can be adopted by authorities having jurisdiction seeking stretch codes building on the methodology of Section C406.*

SECTION CF101—GENERAL

**CF101.1 Purpose.** The purpose of this appendix is to supplement the *International Energy Conservation Code* and requires projects to comply with Advanced Energy Credit Package requirements.

**CF101.2 Scope.** This appendix applies to all buildings that, in accordance with Section C406.1, are required to comply with Section C406.1.1 or C406.1.2.

SECTION CF102—ADVANCED ENERGY CREDIT PACKAGE

**CF102.1 Advanced Energy Credit Package requirements.** The requirements of this section supersede the requirements of Section C406.1.1. Projects shall comply with measures from Section C406.2 to achieve the mini- mum number of required efficiency credits from Table CF102.1(1) based on building occupancy group and *climate zone*. Projects with multiple occupancies, unconditioned parking garages and *buildings* with separate

shell-and-core and build-out construction permits shall comply as follows:

Where a project contains multiple occupancies, credits in Table CF102.1(1) from each building occupancy shall be weighted by the gross floor area to determine the weighted average project energy credits required. Accessory occupancies shall be included with the primary occupancy group for purposes of Section C406 and this appendix.

Exceptions:

1. Unconditioned parking garages that achieve 50 percent of the credits required for use in Groups S-1 and S-2 in Table CF102.1(1).
2. Portions of buildings devoted to manufacturing or industrial use.
3. Where a *building* achieves more renewable and load management credits in Section C406.3 than are required in Section C406.1.2, surplus credits shall be permitted to reduce required energy efficiency credits as follows:

*EECred* = *EECtbl* - {the lesser of: [*SRLMlim*, *SLRMadj* × (*RLMach* - *RLMreq*)]} where:

*EECred* = Reduced required energy efficiency credits.

*EECtbl* = Required energy efficiency credits from Table C406.1.1(1).

*SRLMlim* = Surplus renewable and load management credit limit from Table C406.1.1(2).

*SRLMadj* = 1.0 for all-electric or all-renewable buildings (excluding emergency generation); 0.7 for buildings with fossil fuel equipment (excluding emergency generation).

*RLMach* = Achieved renewable and load management credits from Section C406.3.

*RLMreq* = Required renewable and load management credits from Section C406.1.2.

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE CF102.1(1)—ENERGY CREDIT REQUIREMENTS BY BUILDING OCCUPANCY GROUP** | | | | | | | | | | | | | | | | | | | |
| **BUILDING OCCUPANCY GROUPS** | **CLIMATE ZONE** | | | | | | | | | | | | | | | | | | |
| **0A** | **0B** | **1A** | **1B** | **2A** | **2B** | **3A** | **3B** | **3C** | **4A** | **4B** | **4C** | **5A** | **5B** | **5C** | **6A** | **6B** | **7** | **8** |
| R-2, R-4 and I-1 | 179 | 174 | 188 | 197 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 193 | 200 | 200 | 200 | 200 | 200 | 200 |
| I-2 | 78 | 75 | 73 | 71 | 80 | 90 | 100 | 85 | 90 | 97 | 83 | 90 | 99 | 90 | 96 | 107 | 106 | 130 | 117 |
| R-1 | 106 | 100 | 110 | 105 | 109 | 122 | 123 | 125 | 131 | 137 | 129 | 136 | 157 | 139 | 147 | 171 | 158 | 180 | 176 |
| B | 114 | 110 | 112 | 115 | 108 | 107 | 116 | 111 | 114 | 126 | 118 | 123 | 135 | 125 | 125 | 152 | 142 | 153 | 141 |
| A-2 | 83 | 81 | 82 | 82 | 86 | 86 | 108 | 91 | 97 | 126 | 99 | 111 | 147 | 117 | 113 | 160 | 143 | 163 | 151 |
| M | 113 | 113 | 121 | 118 | 123 | 127 | 116 | 116 | 133 | 109 | 100 | 92 | 99 | 134 | 125 | 171 | 146 | 150 | 137 |
| E | 91 | 95 | 91 | 100 | 96 | 100 | 105 | 104 | 101 | 113 | 110 | 110 | 120 | 117 | 122 | 131 | 132 | 126 | 131 |
| S-1 and S-2 | 108 | 106 | 111 | 109 | 109 | 108 | 89 | 106 | 108 | 134 | 100 | 130 | 200 | 143 | 123 | 200 | 190 | 189 | 148 |
| All other | 54 | 53 | 55 | 56 | 57 | 60 | 61 | 60 | 63 | 68 | 60 | 65 | 73 | 68 | 69 | 84 | 79 | 84 | 78 |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE CF102.1(2)—LIMIT TO ENERGY EFFICIENCY CREDIT CARRYOVER FROM RENEWABLE AND LOAD MANAGEMENT CREDITS** | | | | | | | | | | | | | | | | | | | |
| **BUILDING OCCUPANCY GROUPS** | **CLIMATE ZONE** | | | | | | | | | | | | | | | | | | |
| **OA** | **0B** | **1A** | **1B** | **2A** | **2B** | **3A** | **3B** | **3C** | **4A** | **4B** | **4C** | **5A** | **5B** | **5C** | **6A** | **6B** | **7** | **8** |
| R-2, R-4 and I-1 | 100 | 100 | 114 | 110 | 113 | 91 | 95 | 115 | 101 | 73 | 102 | 99 | 54 | 73 | 101 | 45 | 50 | 66 | 62 |
| I-2 | 30 | 25 | 26 | 20 | 28 | 33 | 38 | 31 | 33 | 37 | 30 | 32 | 41 | 41 | 50 | 53 | 56 | 75 | 80 |
| R-1 | 20 | 8 | 20 | 5 | 26 | 22 | 20 | 28 | 30 | 19 | 26 | 23 | 24 | 28 | 28 | 27 | 30 | 43 | 54 |
| B | 25 | 19 | 18 | 20 | 15 | 15 | 15 | 24 | 25 | 31 | 36 | 32 | 37 | 40 | 43 | 42 | 40 | 51 | 66 |
| A-2 | 9 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 9 | 5 | 5 | 21 | 9 | 5 | 32 | 19 | 49 | 61 |
| M | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 10 |
| E | 24 | 24 | 31 | 29 | 29 | 28 | 19 | 33 | 39 | 31 | 43 | 33 | 34 | 37 | 33 | 31 | 33 | 46 | 54 |
| S-1 and S-2 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 37 | 19 | 5 | 49 | 41 | 51 | 56 |
| All other | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 15 | 5 | 6 | 8 | 5 | 11 | 15 | 5 | 5 | 9 | 20 |

SECTION CF103—BUILDINGS WITHOUT HEAT PUMPS

**CF103.1 Buildings without heat pumps.** The number of efficiency credits required by Section C406.1.1 shall be multiplied by 1.25 for the following:

* 1. Buildings using purchased energy that is not electricity for space heating or service water heating.
  2. Buildings with electric storage water heaters that are not heat pumps.
  3. Buildings with total heat pump space heating capacity less than the space heating load at heating design conditions calcu- lated in accordance with Section C403.1.1.

Exceptions:

* + 1. Portions of buildings devoted to manufacturing or industrial use.
    2. Buildings complying with all of the following:
       1. The building’s peak heating load calculated in accordance with Section C403.1.1 is greater than the building’s peak cooling load calculated in accordance with Section C403.1.1.
       2. The building’s total heat pump space heating capacity is not less than 50 percent of the building’s space heat- ing load at heating design conditions calculated in accordance with Section C403.1.1.
       3. Any energy source other than electricity or on-site renewable energy is used for space heating only where a heat pump cannot provide the necessary heating energy to satisfy the thermostat setting.
       4. Electric resistance heat is used only in accordance with Section C403.4.1.1.
    3. Low-energy buildings complying with Section C402.1.1.1.
    4. Portions of buildings in Utility and Miscellaneous Group U, Storage Group S, Factory Group F or High-Hazard Group H.
    5. Buildings located in Climate Zones 0A, 0B, 1A, 1B, 2A and 2B.

SECTION CF104—EXISTING BUILDINGS

**CF104.1 Additions not served by heat pumps.** The number of efficiency credits required by Section C502.3.7 shall by multiplied by

1.25 for the following:

1. Additions using *purchased energy* that is not electricity for space heating or *service water heating*.
2. Additions served by electric storage water heaters that are not heat pumps.
3. Additions served by total heat pump space heating capacity less than the peak space heating load at heating design condi- tions calculated in accordance with Section C403.1.1.

**Exceptions:** Additions complying with all of the following:

* 1. The *addition’s* peak heating load calculated in accordance with Section C403.1.1 is greater than the *addition’s* peak cool- ing load calculated in accordance with Section C403.1.1.
  2. The *addition’s* total heat pump space heating capacity serving the *addition* is not less than 50 percent of the *addition’s*

space heating load at heating design conditions calculated in accordance with Section C403.1.1.

* 1. Any energy source other than electricity or *on-site renewable energy* is used for space heating serving the *addition* only where a heat pump cannot provide the necessary heating energy to satisfy the *thermostat* setting.
  2. Electric resistance heat serving the *addition* is used only in accordance with Section C403.4.1.1.

### ELECTRIC VEHICLE CHARGING INFRASTRUCTURE



APPENDIX

**CG**

*This Appendix is adopted into the 2025 Illinois Commercial Stretch Energy Code and is mandatory~~. The provisions contained in this appendix are not mandatory unless specifically referenced in the adopting ordinance.~~*

**User notes:**

***~~About this appendix:~~*** *~~Appendix CG can be adopted by authorities having jurisdiction seeking electric vehicle charging infrastructure requirements.~~*

SECTION CG101—ELECTRIC VEHICLE POWER TRANSFER

CG101.1 Definitions.

**AUTOMOBILE PARKING SPACE.** A space within a building or private or public parking lot, exclusive of driveways, ramps, columns, office and work areas, for the parking of an automobile.

**ELECTRIC VEHICLE (EV).** An automotive-type vehicle for on-road use, such as passenger automobiles, buses, trucks, vans, neighborhood electric vehicles and electric motorcycles, primarily powered by an electric motor that draws current from a building electrical service, electric vehicle supply equipment (EVSE), a rechargeable storage battery, a fuel cell, a photovoltaic array or another source of electric current. Plug-in hybrid electric vehicles are electric vehicles having a second source of motive power. Off-road, self-propelled electric mobile equipment, such as industrial trucks, hoists, lifts, transports, golf carts, airline ground support equipment, tractors, boats and the like, are not considered electric vehicles.

**ELECTRIC VEHICLE CAPABLE SPACE (EV CAPABLE SPACE).** A designated automobile parking space that is provided with electrical infrastructure such as, but not limited to, raceways, cables, electrical capacity, a panel-board or other electrical distribution equipment space necessary for the future installation of an EVSE.

**ELECTRIC VEHICLE READY SPACE (EV READY SPACE).** An automobile parking space that is provided with a branch circuit and an outlet, junction box or receptacle that will support an installed EVSE.

**ELECTRIC VEHICLE SUPPLY EQUIPMENT (EVSE).** Equipment for plug-in power transfer, including ungrounded, grounded and equipment grounding conductors; electric vehicle connectors; attached plugs; any personal protection system; and all other fittings, devices, power outlets or apparatus installed specifically for the purpose of transferring energy between the premises wiring and the electric vehicle.

**ELECTRIC VEHICLE SUPPLY EQUIPMENT INSTALLED SPACE (EVSE SPACE).** An automobile parking space that is provided with a dedicated EVSE connection.

**CG101.2 Electric vehicle power transfer infrastructure.** Parking facilities shall be provided with electric vehicle power transfer infrastructure in accordance with Sections CG101.2.1 through CG101.2.6.

**CG101.2.1 Quantity.** The number of required electric vehicle (EV) spaces, *EV capable spaces* and *EV ready spaces* shall be deter- mined in accordance with this section and Table CG101.2.1 based on the total number of *automobile parking spaces* and shall be rounded up to the nearest whole number. For R-2 buildings, the Table CG101.2.1 requirements shall be based on the total number of *dwelling units* or the total number of *automobile parking spaces*, whichever is less.

1. Where more than one parking facility is provided on a *building site*, the number of required *automobile parking spaces*

required to have EV power transfer infrastructure shall be calculated separately for each parking facility.

1. Where one shared parking facility serves multiple building occupancies, the required number of spaces shall be deter- mined proportionally based on the floor area of each building occupancy.
2. Installed electric vehicle supply equipment installed spaces (*EVSE spaces*) that exceed the minimum requirements of this section may be used to meet the minimum requirements for *EV ready spaces* and *EV capable spaces*.
3. Installed *EV ready spaces* that exceed the minimum requirements of this section may be used to meet the minimum requirements for *EV capable spaces*.
4. Where the number of *EV ready spaces* allocated for R-2 occupancies is equal to the number of *dwelling units* or to the number of *automobile parking spaces* allocated to R-2 occupancies, whichever is less, requirements for *EVSE spaces* for R-2 occupancies shall not apply.
5. Requirements for a Group S-2 parking garage shall be determined by the occupancies served by that parking garage. Where new automobile spaces do not serve specific occupancies, the values for Group S-2 parking garage in Table CG101.2.1 shall be used.

**Exception:** Parking facilities serving occupancies other than R2 with fewer than 10 *automobile parking spaces*.

|  |  |  |  |
| --- | --- | --- | --- |
| **TABLE CG101.2.1—REQUIRED EV POWER TRANSFER INFRASTRUCTURE** | | | |
| **OCCUPANCY** | **EVSE SPACES** | **EV READY SPACES** | **EV CAPABLE SPACES** |
| Group A | 10% | 0% | 10% |
| Group B | 15% | 0% | 30% |
| Group E | 15% | 0% | 30% |

|  |  |  |  |
| --- | --- | --- | --- |
| **TABLE CG101.2.1—REQUIRED EV POWER TRANSFER INFRASTRUCTURE—continued** | | | |
| **OCCUPANCY** | **EVSE SPACES** | **EV READY SPACES** | **EV CAPABLE SPACES** |
| Group F | 2% | 0% | 5% |
| Group H | 1% | 0% | 0% |
| Group I | 15% | 0% | 30% |
| Group M | 15% | 0% | 30% |
| Group R-1 | 20% | 5% | 75% |
| Group R-2 | 20% | 5% | 75% |
| Groups R-3 and R-4 | 2% | 0% | 5% |
| Group S exclusive of parking garages | 1% | 0% | 0% |
| Group S-2 parking garages | 15% | 0% | 30% |

**CG101.2.2 EV capable spaces.** Each *EV capable space* used to meet the requirements of Section CG101.2.1 shall comply with the following:

* 1. A continuous raceway or cable assembly shall be installed between an enclosure or outlet located within 3 feet (914 mm) of the *EV capable space* and electrical distribution equipment.
  2. Installed raceway or cable assembly shall be sized and rated to supply a minimum circuit capacity in accordance with Section CG101.2.5.
  3. The electrical distribution equipment to which the raceway or cable assembly connects shall have dedicated overcur- rent protection device space and electrical capacity to supply a calculated load in accordance with Section CG101.2.5.
  4. The enclosure or outlet and the electrical distribution equipment directory shall be marked: “For electric vehicle supply equipment (EVSE).”

**CG101.2.3 EV ready spaces.** Each branch circuit serving *EV ready spaces* used to meet the requirements of Section CG101.2.1 shall comply with the following:

1. Terminate at an outlet or enclosure located within 3 feet (914 mm) of each *EV ready space* it serves.
2. Have a minimum system and circuit capacity in accordance with Section CG101.2.5.
3. The electrical distribution equipment directory shall designate the branch circuit as “For electric vehicle supply equipment (EVSE)” and the outlet or enclosure shall be marked “For electric vehicle supply equipment (EVSE).”

**CG101.2.4 EVSE spaces.** An installed EVSE with multiple output connections shall be permitted to serve multiple *EVSE spaces*. Each EVSE installed to meet the requirements of Section CG101.2.1, serving either a single *EVSE space* or multiple *EVSE spaces*, shall comply with the following:

1. Have a minimum system and circuit capacity in accordance with Section CG101.2.5.
2. Have a nameplate rating not less than 6.2 kW.
3. Be located within 3 feet (914 mm) of each *EVSE space* it serves.
4. Be installed in accordance with Section CG101.2.6.

**CG101.2.5 System and circuit capacity.** The system and circuit capacity shall comply with Sections CG101.2.5.1 and CG101.2.5.2.

**CG101.2.5.1 System capacity.** The electrical distribution equipment supplying the branch circuit(s) serving each *EV capable space*, *EV ready space* and *EVSE space* shall comply with one of the following:

* 1. Have a calculated load of 7.2 kVA or the nameplate rating of the equipment, whichever is larger, for each *EV capable space*, *EV ready space* and *EVSE space*.
  2. Meets the requirements of Section CG101.2.5.3.1.

**CG101.2.5.2 Circuit capacity.** The branch circuit serving each *EV capable space*, *EV ready space* and *EVSE space* shall comply with one of the following:

1. Have a rated capacity not less than 50 amperes or the nameplate rating of the equipment, whichever is larger.
2. Meets the requirements of Section CG101.2.5.3.2.

**CG101.2.5.3 System and circuit capacity management.** Where system and circuit capacity management is selected in Section CG101.2.5.1 or CG101.2.5.2, the installation shall comply with Sections CG101.2.5.3.1 and CG101.2.5.3.2.

**CG101.2.5.3.1 System capacity management.** The maximum equipment load on the electrical distribution equipment supplying the branch circuits(s) serving *EV capable spaces*, *EV ready spaces* and *EVSE spaces* controlled by an energy management system shall be the maximum load permitted by the energy management system, but not less than 3.3 kVA per space.

**CG101.2.5.3.2 Circuit capacity management.** Each branch circuit serving multiple *EVSE spaces*, *EV ready spaces* or *EV capable spaces* controlled by an energy management system shall comply with one of the following:

1. Have a minimum capacity of 25 amperes per space.
2. Have a minimum capacity of 20 amperes per space for R-2 occupancies where all *automobile parking spaces* are *EV ready spaces* or *EVSE spaces*.

**CG101.2.6 EVSE installation.** *EVSE* shall be installed in accordance with NFPA 70 and shall be *listed* and *labeled* in accordance with UL 2202 or UL 2594. *EVSE* shall be accessible in accordance with Section 1107 of the 2024 *International Building Code*.

SECTION CG102—REFERENCED STANDARDS

**CG102.1 General.** See Table CG102.1 for standards that are referenced in various sections of this appendix. Standards are listed by the standard identification with the effective date, standard title, and the section or sections of this appendix that reference the standard.

|  |  |  |
| --- | --- | --- |
| **TABLE CG102.1—REFERENCED STANDARDS** | | |
| **STANDARD ACRONYM** | **STANDARD NAME** | **SECTIONS HEREIN REFERENCED** |
| UL 2202—2009 | *Electric Vehicle (EV) Charging System—with revisions through February 2018* | CG101.2.6 |
| UL 2594—2016 | *Standard for Electric Vehicle Supply Equipment* | CG101.2.6 |

### ELECTRIC-READY COMMERCIAL BUILDING PROVISIONS



APPENDIX

**CH**

*The provisions contained in this appendix are not mandatory unless specifically referenced in the adopting ordinance.*

**User notes:**

***About this appendix:*** *Appendix CH can be adopted where authorities having jurisdiction seek new building to be electric ready.*

SECTION CH101—GENERAL

**CH101.1 Intent.** The intent of this appendix is to amend the *International Energy Conservation Code* to reduce future retrofit costs by requiring *commercial buildings* with combustion equipment to install the electrical infra- structure for electric equipment.

**CH101.2 Scope.** The provisions in this appendix are applicable to *commercial buildings*. New construction shall comply with Section CH103.

SECTION CH102—DEFINITIONS

**APPLIANCE.** A device or apparatus that is manufactured and designed to utilize energy and for which this code provides specific requirements.

**COMBUSTION EQUIPMENT.** Any equipment or appliance used for space heating, service water heating, cooking, clothes drying or lighting that uses a fossil fuel.

**COMMERCIAL COOKING APPLIANCES.** Commercial cooking appliances used in a commercial food service establishment for heating or cooking food and which produce grease vapors, steam, fumes, smoke or odors that are required to be removed through a local exhaust ventilation system. Such appliances include deep fat fryers, upright broilers, griddles, broilers, steam-jacketed kettles, hot- top ranges, under-fired broilers (charbroilers), ovens, barbecues, rotisseries and similar appliances.

SECTION CH103—NEW COMMERCIAL BUILDING

**CH103.1 Additional electric infrastructure.** Electric infrastructure in *buildings* that contain combustion equipment shall be installed in accordance with this section.

**CH103.1.1 Combustion space heating.** Spaces containing combustion equipment for space heating shall comply with Sections CH103.1.1.1, CH103.1.1.2 and CH103.1.1.3.

|  |  |  |
| --- | --- | --- |
| **TABLE CH103.1.1—ALTERNATE ELECTRIC SPACE HEATING EQUIPMENT CONVERSION FACTORS (VA/kBtu/h)** | | |
| **99.6% HEATING DESIGN TEMPERATURE** | | ***Ps*** |
| **Greater Than (°F)** | **Not Greater Than** | **VA/kBtu/h** |
| 50 | N/A | N/A |
| 45 | 50 | 94 |
| 40 | 45 | 100 |
| 35 | 40 | 107 |
| 30 | 35 | 115 |
| 25 | 30 | 124 |
| 20 | 25 | 135 |
| 15 | 20 | 149 |
| 10 | 15 | 164 |
| 5 | 10 | 184 |
| 0 | 5 | 210 |
| -5 | 0 | 243 |
| -10 | -5 | 289 |
| -15 | -10 | 293 |
| For SI: °C = [(° F) – 32]/1.8, 1 British thermal unit per hour = 0.2931 kW. | | |

**CH103.1.1.1 Designated exterior locations for future electric space-heating equipment.** Spaces containing combustion equipment for space heating shall be provided with designated exterior location(s) shown on the plans and of sufficient size

for outdoor space-heating heat pump equipment, with a chase that is sized to accommodate refrigerant lines between the exterior location and the interior location of the space-heating equipment, and with natural drainage for condensate from heating operation or a condensate drain located within 3 feet (914 mm) of the location of the future exterior space-heating heat pump equipment.

**CH103.1.1.2 Dedicated branch circuits for future electric space-heating equipment.** Spaces containing combustion space- heating equipment with a capacity not more than 65,000 Btu/h (19 kW) shall be provided with a dedicated 240-volt branch circuit with ampacity of not less than 50. The branch circuit shall terminate within 6 feet (1829 mm) of the space heating equip- ment and be in a location with ready *access*. Both ends of the branch circuit shall be labeled with the words “For Future Electric Space Heating Equipment” and be electrically isolated. Spaces containing combustion equipment for space heating with a capacity of not less than 65,000 Btu/h (19 kW) shall be provided with a dedicated branch circuit rated and sized in accordance with Section CH103.1.1.3, and terminating in a junction box within 3 feet (914 mm) of the location the space heating equipment in a location with ready *access*. Both ends of the branch circuit shall be labeled “For Future Electric Space Heating Equipment.”

Exceptions:

1. Where a branch circuit provides electricity to the space heating combustion equipment and is rated and sized in accordance with Section CH103.1.1.3.
2. Where a branch circuit provides electricity to space cooling equipment and is rated and sized in accordance with Section CH103.1.1.3.
3. Where future electric space heating equipment would require three-phase power and the space containing combustion equipment for space heating is provided with an electrical panel with a label stating “For Future Elec- tric Space Heating Equipment” and a bus bar rated and sized in accordance with Section CH103.1.1.3.
4. Buildings where the 99.6 percent design heating temperature is not less than 50°F (10°C).

**CH103.1.1.3 Additional space heating electric infrastructure sizing.** Electric infrastructure for future electric space heating equipment shall be sized to accommodate not less than one of the following:

* 1. An electrical capacity not less than the nameplate space heating combustion equipment heating capacity multiplied by the value in Table CH103.1.1, in accordance with Equation CH-1.

**Equation CH-1** *VAS* = *Qcom* × *PS*

*VAs* = The required electrical capacity of the electrical infrastructure in volt-amps. *Qcom* = The nameplate heating capacity of the combustion equipment in kBtu/h. *Ps* = The VA per kBtu/h from Table CH103.1.1 in VA/kBtu/h.

* 1. An electrical capacity not less than the peak space heating load of the building areas served by the space heating combustion equipment, calculated in accordance with Section C403.1.1, multiplied by the value for the 99.6 percent design heating temperature in Table CH103.1.1, in accordance with Equation CH-2.

**Equation CH-2** *VAS* = *Qdesign* × *PS*

*VAs* = The required electrical capacity of the electrical infrastructure in volt-amps.

*Qdesign* = The 99.6 percent design heating load of the spaces served by the combustion equipment in kBtu/h.

*Ps* = The VA per kBtu/h from Table CH103.1.1 in VA/kBtu/h.

* 1. An *approved* alternate design that uses no energy source other than electricity or *on-site renewable energy*.

**CH103.1.2 Combustion service water heating** Spaces containing combustion equipment for *service water heating* shall comply with Sections CH103.1.2.1, CH103.1.2.2 and CH103.1.2.3.

|  |  |  |
| --- | --- | --- |
| **TABLE CH103.1.2—ALTERNATE ELECTRIC WATER HEATING EQUIPMENT CONVERSION FACTORS (VA/kBtu/h)** | | |
| **99.6% HEATING DESIGN TEMPERATURE** | | ***Pw*** |
| **Greater Than (°F)** | **Not More Than** | **VA/kBtu/h** |
| 55 | 60 | 118 |
| 50 | 55 | 123 |
| 45 | 50 | 129 |
| 40 | 45 | 136 |
| 35 | 40 | 144 |
| 30 | 35 | 152 |
| 25 | 30 | 162 |
| 20 | 25 | 173 |
| 15 | 20 | 185 |

**APPENDIX CH—ELECTRIC-READY COMMERCIAL BUILDING PROVISIONS**

|  |  |  |
| --- | --- | --- |
| **TABLE CH103.1.2—ALTERNATE ELECTRIC WATER HEATING EQUIPMENT CONVERSION FACTORS (VA/kBtu/h)—continued** | | |
| **99.6% HEATING DESIGN TEMPERATURE** | | ***Pw*** |
| **Greater Than (°F)** | **Not More Than** | **VA/kBtu/h** |
| 10 | 15 | 293 |
| 5 | 10 | 293 |
| 0 | 5 | 293 |
| Less than 0°F | | 293 |
| For SI: °C = [(°F) – 32]/1.8, 1 British thermal unit per hour = 0.2931 kW. | | |

**CH103.1.2.1 Combustion service water heating electrical infrastructure.** For each piece of combustion equipment for water heating with an input capacity of not more than 75,000 Btu/h (22 kW), the following electrical infrastructure is required:

* + 1. An individual 240-volt branch circuit with an ampacity of not less than 30 shall be provided and terminate within 6 feet (1829 mm) of the water heater and shall be in a location with ready access.
    2. The branch circuit overcurrent protection device and the termination of the branch circuit shall be labeled “For future electric water heater.”
    3. The space for containing the future water heater shall include the space occupied by the combustion equipment and shall have a height of not less than 7 feet (2134 mm), a width of not less than 3 feet (914 mm), a depth of not less than 3 feet (914 mm) and with a volume of not less than 700 cubic feet (20 m3).

**Exception:** Where the space containing the water heater provides for air circulation sufficient for the operation of a heat pump water heater, the minimum room volume shall not be required.

**CH103.1.2.2 Designated locations for future electric heat pump water heating equipment.** Designated locations for future electric heat pump water heating equipment shall be in accordance with one of the following:

1. Designated exterior location(s) shown on the plans, of sufficient size for outdoor water heating heat pump equipment and with a chase that is sized to accommodate refrigerant lines between the exterior location and the interior loca- tion of the water heating equipment.
2. An interior location with a minimum volume the greater of 700 cubic feet (19 822 L) or 7 cubic feet (198 L) per 1,000 Btu/h (293 W) combustion equipment water heating capacity. The interior location shall include the space occupied by the combustion equipment.
3. An interior location with sufficient airflow to exhaust cool air from future water heating heat pump equipment provided by not fewer than one 16-inch (406 mm) by 24-inch (610 mm) grill to a heated space and one 8-inch (203 mm) *duct* of not more than 10 feet (3048 mm) in length for cool exhaust air.

**CH103.1.2.3 Dedicated branch circuits for future electric heat pump water heating equipment.** Spaces containing combustion equipment for water heating with a capacity of greater than 75,000 Btu/h (21 980 W) shall be provided with a dedi- cated branch circuit rated and sized in accordance with Section CH103.1.2.4 and terminating in a junction box within 3 feet (914 mm) of the location the water heating equipment in a location with ready *access*. Both ends of the branch circuit shall be labeled “For Future Electric Water Heating Equipment.”

**Exception:** Where future electric water heating equipment would require three-phase power and the main electrical service panel has a reserved space for a bus bar rated and sized in accordance with Section CH103.1.2.4 and labeled “For Future Elec- tric Water Heating Equipment.”

**CH103.1.2.4 Additional water heating electric infrastructure sizing.** Electric infrastructure water heating equipment with a capacity of greater than 75,000 Btu/h (21 980 W) shall be sized to accommodate one of the following:

1. An electrical capacity not less than the combustion equipment water heating capacity multiplied by the value in Table CH103.1.2 plus electrical capacity to serve recirculating loads as shown in Equation CH-3.

*VAW* = (*Qcapacity* × *PW*) + [*Qrecirc* × 293(*VA*(Btu/h))]

1. An alternate design that complies with this code, is *approved* by the authority having jurisdiction and uses no energy source other than electricity or *on-site renewable energy****.***

**CH103.1.3 Combustion cooking.** Spaces containing combustion equipment for cooking shall comply with Section CH103.1.3.1 or CH103.1.3.2.

**CH103.1.3.1 Commercial cooking.** Spaces containing commercial cooking appliances shall be provided with a dedicated branch circuit with a minimum electrical capacity in accordance with Table CH103.1.3.1 based on the appliance in the space. The branch circuit shall terminate within 3 feet (914 mm) of the appliance in a location with ready *access*. Both ends of the branch circuit shall be labeled with the words “For Future Electric Cooking Equipment” and be electrically isolated.

|  |  |
| --- | --- |
| **TABLE CH103.1.3.1—COMMERCIAL COOKING MINIMUM BRANCH CIRCUIT CAPACITY** | |
| **COMMERCIAL COOKING APPLIANCE** | **MINIMUM BRANCH CIRCUIT CAPACITY** |
| Range | 469 VA/kBtu/h |
| Steamer | 114 VA/kBtu/h |
| Fryer | 200 VA/kBtu/h |
| Oven | 266 VA/kBtu/h |
| Griddle | 195 VA/kBtu/h |
| All other commercial cooking appliances | 114 VA/kBtu/h |
| For SI: 1 British thermal unit per hour = 0.2931 kW. | |

**CH103.1.3.2 All other cooking.** Spaces containing all other cooking equipment not designated as commercial cooking appli- ances shall be provided with a dedicated branch circuit in compliance with NFPA 70 Section 422.10. The branch circuit shall terminate within 6 feet (1829 mm) of fossil fuel ranges, cooktops and ovens and be in a location with ready *access*. Both ends of the branch circuit shall be labeled with the words “For Future Electric Cooking Equipment” and be electrically isolated.

**CH103.1.4 Combustion clothes drying.** Spaces containing combustion equipment for clothes drying shall comply with Section CH103.1.4.1 or CH103.1.4.2.

**CH103.1.4.1 Commercial drying.** Spaces containing clothes drying equipment and end uses for commercial laundry applica- tions shall be provided with conduit that is continuous between a junction box located within 3 feet (914 mm) of the equipment and an electrical panel. The junction box, conduit and bus bar in the electrical panel shall be rated and sized to accommodate a branch circuit with sufficient capacity for equivalent electric equipment with equivalent equipment capacity. The electrical junction box and electrical panel shall have labels stating, “For Future Electric Clothes Drying Equipment.”

**CH103.1.4.2 Residential drying.** Spaces containing clothes drying equipment, appliances and end uses serving multiple *dwelling units* or sleeping areas with a capacity less than or equal to 9.2 cubic feet (0.26 m3) shall be provided with a dedicated 240-volt branch circuit with a minimum capacity of 30 amperes, shall terminate within 6 feet (1829 mm) of fossil fuel clothes dryers and shall be in a location with ready *access*. Both ends of the branch circuit shall be labeled with the words “For Future Electric Clothes Drying Equipment” and be electrically isolated.

**CH103.1.5 On-site transformers.** *Enclosed spaces* and underground vaults containing on-site electric transformers on the *build- ing* side of the electric utility meter shall have sufficient space to accommodate transformers sized to serve the additional electric loads identified in Sections CH103.1.1, CH103.1.2, CH103.1.3 and CH103.1.4.

**CH103.2 Hydronic heating design requirements.** For all hydronic space heating systems, the design entering water temperature for coils, radiant panels, radiant floor systems, radiators, baseboard heaters and any other device that uses hot water to provide heat to a space shall be not more than 130°F (54°C).

**CH103.3 Construction documentation.** The *construction documents* shall provide details for additional electric infrastructure, including branch circuits, conduit, prewiring, panel capacity and electrical service capacity, as well as interior and exterior spaces designated for future electric equipment.

### DEMAND RESPONSIVE CONTROLS



APPENDIX

**CI**

*This Appendix is adopted into the 2025 Illinois Commercial Stretch Energy Code and is mandatory ~~The provisions contained in this appendix are not mandatory unless specifically referenced in the adopting ordinance.~~*

**User notes:**

***~~About this appendix:~~*** *~~Appendix CI can by adopted by authorities having jurisdiction seeking demand responsive controls to be integrated into heating and cooling systems, water heating systems and lighting systems.~~*

SECTION CI101—DEMAND RESPONSIVE HEATING AND COOLING SYSTEMS

**CI101.1 Demand responsive controls.** Electric heating and cooling systems shall be provided with demand responsive controls capable of executing the following actions in response to a *demand response signal*:

1. Automatically increasing the zone operating cooling setpoint by the following values: 1°F (0.5°C), 2°F (1°C), 3°F (1.5°C) and 4°F (2°C).
2. Automatically decreasing the zone operating heating setpoint by the following values: 1°F (0.5°C), 2°F (1°C), 3°F (1.5°C) and 4°F (2°C).

Where a *demand response signal* is not available, the heating and cooling system controls shall be capable of performing all other functions. Where *thermostats* are controlled by direct digital control including, but not limited to, an energy management system, the system shall be capable of *demand responsive control* and capable of adjusting all thermal setpoints to comply. The demand responsive controls shall comply with either Section CI101.1.1 or CI101.1.2.

Exceptions:

* 1. Group I occupancies.
  2. Group H occupancies.
  3. Controls serving data center systems.
  4. Occupancies or applications requiring precision in indoor temperature control as approved by the code official.
  5. Buildings that comply with Load Management measure G02 in Section C406.3.3.
  6. Buildings with energy storage capacity for not less than a 25 percent load reduction at peak load for a period of not less than 3 hours.

**CI101.1.1 Air conditioners and heat pumps with two or more stages of control and cooling capacity of less than 65,000 Btu/h.** *Thermostats* for air conditioners and heat pumps with two or more stages of control and a cooling capacity less than 65,000 Btu/h (19 kW) shall be provided with a *demand responsive control* that complies with the communication and performance requirements of AHRI 1380.

**CI101.1.2 All other heating and cooling systems.** *Thermostats* for heating and cooling systems shall be provided with a *demand responsive control* that complies with one of the following:

1. Certified OpenADR 2.0a VEN, as specified under Clause 11, Conformance.
2. Certified OpenADR 2.0b VEN, as specified under Clause 11, Conformance.
3. Certified by the manufacturer as being capable of responding to a *demand response signal* from a certified OpenADR 2.0b VEN by automatically implementing the control functions requested by the VEN for the equipment it controls.
4. IEC 62746-10-1.
5. The communication protocol required by a controlling entity, such as a utility or service provider, to participate in an automated demand response program.
6. The physical configuration and communication protocol of ANSI/CTA 2045-A or ANSI/CTA 2045-B.

SECTION CI102—DEMAND RESPONSIVE WATER HEATING

**CI102.1 Demand responsive water heating.** Electric storage water heaters with a rated water storage volume of 40 gallons (151 L) to 120 gallons (454 L) and a nameplate input rating equal to or less than 12 kW shall be provided with demand responsive controls in accordance with Table CI102.1.

Exceptions:

1. Water heaters that provide a hot water delivery temperature of 180°F (82°C) or greater.
2. Water heaters that comply with Section IV, Part HLW or Section X of the ASME *Boiler and Pressure Vessel Code.*
3. Water heaters that use three-phase electric power.

|  |  |  |
| --- | --- | --- |
| **TABLE CI102.1—DEMAND RESPONSIVE CONTROLS FOR WATER HEATING** | | |
| **EQUIPMENT TYPE** | **CONTROLS** | |
| **Manufactured before 7/1/2025** | **Manufactured on or after 7/1/2025** |
| Electric storage water heaters | AHRI Standard 1430 or ANSI/CTA-2045-B Level 1 and also capable of initiating water heating to meet the temperature setpoint in response to a demand response signal | AHRI Standard 1430 |

SECTION CI103—DEMAND RESPONSIVE LIGHTING CONTROLS

**CI103.1 Demand responsive lighting controls.** Interior general lighting in Group B, E, M and S occupancies shall have demand responsive controls complying with Section C405.2.8.1 in not less than 75 percent of the interior floor area.

Exceptions:

1. Where the combined interior floor area of Group B, E, M and S occupancies is less than 10,000 square feet (929 m2).
2. Buildings where a *demand response signal* is not available from a controlling entity other than the *owner*.
3. Parking garages.
4. Ambulatory care facilities.
5. Outpatient clinics.
6. Physician or dental offices.

SECTION CI104—REFERENCED STANDARDS

**CI104.1 General.** See Table CI104.1 for standards that are referenced in various sections of this appendix. Standards are listed by the standard identification with the effective date, standard title, and the section or sections of this appendix that reference the standard.

|  |  |  |
| --- | --- | --- |
| **TABLE CI104.1—REFERENCED STANDARDS** | | |
| **STANDARD ACRONYM** | **STANDARD NAME** | **SECTIONS HEREIN REFERENCED** |
| AHRI 1430 (I-P)—2022 | *Demand Flexible Electric Storage Water Heaters (with Addendum 1)* | Table CI102.1 |
| ASME BPVC | *Boiler and Pressure Vessel Code* | CI102.1 |

### ELECTRICAL ENERGY STORAGE SYSTEM



APPENDIX

**CJ**

*This Appendix is adopted into the 2025 Illinois Commercial Stretch Energy Code and is mandatory ~~The provisions contained in this appendix are not mandatory unless specifically referenced in the adopting ordinance.~~*

**User notes:**

***~~About this appendix:~~*** *~~This voluntary appendix provides requirements for electric energy storage readiness provisions.~~*

SECTION CJ101—ELECTRICAL ENERGY STORAGE SYSTEM

**CJ101.1 Electrical energy storage system.** Buildings shall comply with Section CJ101.1.3 and either Section CJ101.1.1 or CJ101.1.2.

**CJ101.1.1 Electrical energy storage system (ESS) capacity.** Each building shall have one or more ESS with a total rated energy capacity and rated power capacity as follows:

* 1. ESS-rated energy capacity (kWh) ≥ 1.0 × installed on-site renewable electric energy system rated power (kWDC).
  2. ESS-rated power capacity (kW) ≥ 0.25 × installed on-site renewable electric energy system rated power (kWDC).

Where installed, DC-coupled battery systems shall meet the requirements for rated energy capacity alone.

**CJ101.1.2 Electrical energy storage system (ESS) ready.** Each building shall have one or more reserved

ESS-ready areas to accommodate future electrical storage ~~in accordance with Sections CJ101.1.2.1 through CJ101.1.2.4~~.

**CJ101.1.3 Electrical energy storage installed or -ready area.** Areas where ESS is installed and ESS-ready areas shall comply with Sections CJ101.1.2.1 through CJ101.1.2.4.

**CJ101.1.2.1 ESS-installed or -ready location.** Each ESS-installed or -ready area shall be located in accordance with Section 1207 of the 2024 *International Fire Code or NFPA 855*. For the purposes of locating and designing means of egress, ESS-installed or ready areas shall comply with either (1) means of egress requirements for Group H occupancies of the

2024 International Fire Code or (2) Sections 7.2.1.4.2(3) and 7.11 of NFPA 101 (2015).

**CJ101.1.2.2 ESS-installed or -ready minimum area requirements.** Each ESS-installed or -ready area shall be sized in accordance with the spacing requirements of Section 1207 of the 2024 *International Fire Code or NFPA 855* and the UL 9540 or UL 9540A designated rating of the planned system. Where rated to UL 9540A, the area shall be sized in accordance with the manufacturer’s instructions.

**CJ101.1.2.3 Electrical distribution equipment.** The on-site electrical distribution equipment shall have sufficient capacity, rating and space to allow the installation of overcurrent devices and circuit wiring in accordance with NFPA 70 for future elec- trical ESS complying with the capacity criteria of Section CJ101.1.2.4.

**CJ101.1.2.4 ESS-installed or -ready minimum system capacity.** Compliance with ESS-installed or -ready requirements in Sections CJ101.1.2.1 through CJ101.1.2.3 shall be based on a minimum total energy capacity and minimum rated power capacity as follows:

* + 1. ESS-rated energy capacity (kWh) ≥ gross conditioned floor area of the three largest floors (ft2) × 0.0008 kWh/ft2.
    2. ESS-rated power capacity (kW) ≥ gross conditioned floor area of the three largest floors (ft2) × 0.0002 kW/ft2.

SECTION CJ102—REFERENCED STANDARDS

**CJ102.1 General.** See Table CJ102.1 for standards that are referenced in various sections of this appendix. Standards are listed by the standard identification with the effective date, standard title, and the section or sections of this appendix that reference the standard.

|  |  |  |
| --- | --- | --- |
| **TABLE CJ102.1—REFERENCED STANDARDS** | | |
| **STANDARD ACRONYM** | **STANDARD NAME** | **SECTIONS HEREIN REFERENCED** |
| ANSI/CAN/UL 9540—2020 | *Energy Storage Systems and Equipment* | CJ101.1.2.2 |
| ANSI/CAN/UL 9540A—2019 | *Test Method for Evaluating Runaway Fire Propagation Energy Storage Systems* | CJ101.1.2.2 |

**Above-Grade Wall** C202 **Access (To)** C202 **Accessible**

Controls C402.2.3, C404.6, C404.8.1, C405.2.4.1

Defined C202

**Addition** C202

**Additional Efficiency Package** C406

**Additions**

Defined C202

Historic buildings C501.5 Requirements C502

**Administration**

**Air Barrier** C402.6.1

Access openings C402.6.4 Assemblies C402.6.2.3.2 Compliance options C402.6.2 Construction C402.6.1.2 Dampers C403.7.7

Doors other than fenestration C402.6.4

Fenestration C402.6.3, Table C402.6.3 Materials C402.6.2.3.1

Penetrations C402.6.1.2 Recessed lighting C402.6.1.2.1

Rooms with fuel-burning appliances C402.1.5

Testing C402.6 Vestibules C402.6.6

**Air Conditioners** C403.3.2, C403.4.4 Efficiency requirements

Table C403.3.2(1), Table C403.3.2(3), Table C403.3.2(4), Table C403.3.2(8), Table C403.3.2(10),

Table C403.3.2(16)

**Air Curtain**

Defined C202 Vestibules C402.6.6

**Air Curtain Unit** C202

**Air Economizers**

Defined C202

Requirements C403.5, C403.5.1, C403.5.2, C403.5.3, C403.5.4

**Air Intakes and Exhausts** C402.6.5, C403.7.7

**Air Leakage** C202, C402.6

**Air System Balancing** C408.2.2.1, C408.2.2.2, C408.2.5.1

**Alteration** C106.5, C202, C401.2.1, C501.1, C501.2, C501.5, C503, C503.2, C503.3, C503.4, C503.5

**Alternative Materials** C104

**Approved**

Defined C202

**Approved Agency**

Defined C202 Inspections C106.5

**Approved Source** C202

**Area-Weighted *U*-Factor** C402.5.3.4

**Automatic**

Defined C202

**Basement Walls**

**(see also Wall, Below Grade)** C401.3

**Below-Grade Wall**

**(see Wall, Below Grade)**

**Best Efficiency Point (BEP)** C202, C403.17

**Biogas** C202

### TOTAL BUILDING PERFORMANCE PATHWAY



APPENDIX

**CK**

*This Appendix is adopted into the 2025 Illinois Commercial Stretch Code and is mandatory. ~~The provisions contained in this appendix are not mandatory unless specifically referenced in the adopting ordinance.~~*

**User notes:**

***~~About this appendix:~~*** *~~Appendix CH can be adopted where authorities having jurisdiction seek new building to be electric ready.~~*

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SECTION CK101—SCOPE  This section establishes criteria for *building*s that demonstrate compliance using total building performance utilizing site energy in accordance with Section 4.2.1.1 of ANSI/ASHRAE/IESNA 90.1.  SECTION CK102—COMPLIANCE BASED ON SITE ENERGY  *Buildings* shall comply with ANSI/ASHRAE/IESNA 90.1 as modified by this section.  **CK102.1 Terms.** For the purposes of compliance with this appendix, terminology in ANSI/ASHRAE/IESNA 90.1 shall be modified as follows:   1. Replace references to energy cost with references to site energy in Sections G1.2.2, G1.3.2, G2.1, G2.5 and G2.4.2 section headings. 2. *Baseline building performance* shall be defined as “the annual *site energy* for a building design intended for use as a baseline for rating above-standard design or when using the *Performance Rating Method* as an alternative path for minimum standard compliance in accordance with Section 4.2.1.1.” 3. *Proposed building performance* shall be defined as “the annual site energy calculated for a *proposed design*.”   **CK102.2 Section 4.2.1.1.** Section 4.2.1.1 shall be replaced with the following:  New buildings shall comply with Sections 4.2.2 through 4.2.5 and either the provisions of:   1. Sections 5, “Building Envelope”; 6, “Heating, Ventilating, and Air Conditioning”; 7, “Service Water Heating”; 8, “Power”; 9, “Lighting”; 10, “Other Equipment”; and 11, “Additional Efficiency Requirements,” or 2. Normative Appendix G, “Performance Rating Method.”   When using Normative Appendix G, the Performance Index (Site Energy) of new *buildings, additions* to *existing buildings* and/or alterations to existing buildings shall be less than or equal to the Performance Index Target (PIt) when calculated in accordance with the following:  PIt = [BBUE + (BPFsite × BBRE) – PRE]/BBP  where:  PI = Performance Index (Site Energy) calculated in accordance with Section G1.2.  BBUE = Baseline *building* unregulated site *energy*, which is the portion of the annual site *energy* of a *baseline building*  *design* that is due to *unregulated energy use*.  BBRE = Baseline *building* regulated site energy, which is the portion of the annual site *energy* of a *baseline*  *building design* that is due to *regulated energy use*.  BPFsite = *Building* performance factor from Table 4.2.1.1. For *building* area types not listed in Table 4.2.1.1, use “All  others.” Where a *building* has multiple *building* area types, the required BPF shall be equal to the area-weighted  average of the *building* area types, based on their gross floor area. Where a project includes an *existing building*  and an *addition*, the required BPF shall be equal to the area-weighted average, based on the *gross floor area*, of  the *existing building* BPF, determined as described in Section 4.2.1.3, and the *addition* BPF from Table 4.2.1.1.  BBP = Baseline *building* performance.  PBP = *Proposed building performance*, including the reduced annual site *energy* associated with all *on-site renewable*  *energy* generation systems.  PBPnre *= Proposed building performance* without any credit for reduced annual *energy* from *on-site renewable energy*  generation systems.  PBPpre = *Proposed building performance*, excluding any *renewable energy system* in the *proposed design* and including an  *on-site renewable energy system* that meets but does not exceed the requirements of Section 10.5.1.1 modeled  following the requirements for a *budget building design* in Table 12.5.1.  PRE = PBPnre – PBPpre  When (PBPpre – PBP)/BBP > 0.05, new buildings, additions to existing buildings and/or alterations to existing buildings shall comply with the following:  P~~C~~SEI + [(PBPnre – PBP)/BBP] – 0.05 < P~~C~~SEIt  When (PBPpre – PBP)/BBP > 0.05, new buildings, additions to existing buildings and/or alterations to existing buildings shall comply with the following:  PCI + [(PBPpre – PBP)/BBP] – 0.05 < PCIt  ***Informative Notes:***   1. PBPnre = *Proposed building performance*, no renewable *energy* 2. PBPpre = *Proposed building performance*, prescriptive renewable energy 3. PRE = Prescriptive renewable energy   **CK102.3 Building performance factors.** Table 4.2.1.1 Building Performance Factor (BPF) shall be replaced with Table CK102.3.  **TABLE CK102.3**  **BUILDING PERFORMANCE FACTORS (BPF), SITE ENERGY**   |  |  |  | | --- | --- | --- | | **BUILDING AREA TYPE** | **CLIMATE ZONE** | | | **4A** | **5A** | | Multifamily | 0.61 | 0.56 | | Healthcare/hospital | 0.62 | 0.65 | | Hotel/motel | 0.65 | 0.63 | | Office | 0.47 | 0.49 | | Restaurant | 0.66 | 0.69 | | Retail | 0.47 | 0.52 | | School | 0.42 | 0.44 | | Warehouse | 0.38 | 0.46 | | All others | 0.55 | 0.57 |   **CK102.4 Section G1.2.2.** Section G1.2.2 shall be replaced with the following:  The performance of the *proposed design* is calculated in accordance with the provisions of this appendix using the following formula:  Performance Site *Energy* Index = *Proposed building performance/Baseline building performance*  Both the *proposed building performance* and the *base- line building performance* shall include all end-use load components within and associated with the *building* when calculating the Performance Site *Energy* Index.  **CK102.5 Section G1.3.2.** Item a in Section G1.3.2 shall be replaced as follows:   1. The following documentation shall be submitted to the *rating authority*: the *simulation program* used, the version of the *simulation program* and the results of the *energy* analysis, including the calculated values for the baseline *building* unregulated site *energy* (BBUE), baseline *building* regulated site *energy* (BBRE), *Building* Performance Factor (BPF), *baseline building performance*, the *proposed building performance*, Performance Site *Energy* Index (PSEI) and Performance Site *Energy* Index Target (PIt).   **CK102.6 Section G2.4.2.** Section G2.4.2 shall be renamed “Annual Site Energy.” The informative note for Sections G2.4.2 and G2.4.2.2 shall be removed. The first sentence in Section G2.4.2 shall be replaced with the following:  The *baseline building performance* and *proposed building performance* shall be determined using conversion factors in Table CI102.6.  **TABLE CK102.6**  **UNITS OF FUEL TO SITE ENERGY CONVERSION FACTORS**   |  |  |  | | --- | --- | --- | | **BUILDING PROJECT ENERGY SOURCE** | **UNITS** | **SITE ENERGY Btu/unit (W-h/unit)** | | Electricity | kWh | 3,412 | | Natural gas | Therm (GJ) | 100,000 (277,778) | | Propane | Therm (GJ) | 100,000 (277,778) | | Distillate fuel oil | Gallon (L) | 137,600 (10,651) |   **CK102.7 Section G2.5.** Section G2.5, Item e shall be replaced with the following:  e. The Performance Site Energy Index calculated with and without the exceptional calculation method. |  |
|  |  |

|  |  |
| --- | --- |
|  |  |

### INDEX

**Biomass** C202 **Biomass Waste** C202 **Board of Appeals** C109

Limitations on authority C109.2 Qualifications of members C109.3

**Boiler, Modulating** C202 **Boiler System** C202 **Boilers**

Defined C202

Requirements Table C403.3.2(6), C403.3.4.2, C403.4.3, C404.2,

Table C404.2

Setback controls C403.4.1.6 Turndown controls C403.3.4.2

**Bubble Point** C202, Table C403.3.2(7)

**Building**

Defined C202

**Building Commissioning** Defined C202 Requirements C408

**Building Entrance**

Defined C202

Exterior lighting Table C405.5.2(2) Vestibules C402.6.6

**Building Envelope**

Compliance documentation C105.2, C105.2.1

Defined C202

Exemptions C402.1.1, C402.1.1.3 Insulation C303.1.1

Insulation and fenestration criteria C402.1.3, Table C402.1.3, C402.1.2,

Table C402.1.2 Performance method C407.2 Requirements C402

**Building Site** C202

**Building Thermal Envelope**

Air leakage and barriers C402.6 Defined C202

Doors C402.5.5

Low-energy buildings C402.1.1 Performance C402.1, C402.1.3,

C402.1.2, C402.1.4

Rooms with fuel-burning appliances C402.1.5

Specific insulation C402.2

**Captive Key Override** C202, C405.2.10.1

**Caulking and Weatherstripping** C402.6.1.2, C402.6.4, C402.6.7, C402.6.1.2.1

**Cavity Insulation** C202

***C*-Factor (Thermal Conductance)**

Assembly *U*-, *C*- or *F*-factor method Table C402.1.2, C402.1.2

Defined C202

**Change of Occupancy** C501.2, C505

**Chi-Factor (-Factor)** C202, C402.1.4, Table C402.1.4

**Chillers** Table C403.3.2(3), Table C407.4.1(3)

Positive displacement chilling packages C403.3.2.2

Water-cooled centrifugal chiller packages Table C403.3.2(3), Table C407.4.1(5)

**Circulating Hot Water System**

Defined C202

Requirements C404.6.1, C404.6.3 **Circulating Pumps** C403.4.3.3 **Circulating Systems** C403.4.3.3, C404.6 **Clean Water Pump** C202, C403.17 **Climate Types**

Defined Table C301.3

**Climate Zone** C202

**Climate Zones** Figure C301.1,

Table C301.1, C301.3, Table C301.3

International climate zones Table C301.3

**Code Official**

Approval of alternate methods C104.1 Defined C202

Examination of construction documents C105.3

Inspections C107

**Coefficient of Performance (COP)**

Requirements Table C403.3.2(2), Table C403.3.2(3)

**Coefficient of Performance (COP) − Cooling** C202

**Coefficient of Performance (COP) − Heating** C202

**Commercial Building** C202

**Commercial Buildings**

Compliance C101.2, C101.4, C102.1.1, C401.1, C401.2, Chapter 5

Defined C202 **Commissioning** C408 **Common Area** C202

**Community Renewable Energy Facility** C202

**Compliance and Enforcement** Existing buildings C501.2 General C101.4

**Component Performance Method**

C402.1.4

**Compressor (Refrigeration) Systems**

C403.12.3.2

**Computer Room**

Air conditioning Table C403.3.2(10) Defined C202

Electrical equipment C405.9 **Condensing Unit** C202 **Condensing Units**

Defined C202 Efficiency requirements

Table C403.3.2(1), Table C403.3.2(10)

**Conditioned Floor Area**

Defined C202

**Conditioned Space**

Change from nonconditioned or low energy C502.2

Defined C202

Roof solar reflectance C402.4 Rooms containing fuel-burning

appliances C402.1.5 **Congregate Living Facilities** C202 **Construction Documents** C105

Amended C105.4 Approval C105.3.1 Examination C105.3

Information required C105.2 Phased approvals C105.3.3 Previous approvals C105.3.2 Retention C105.5 Revocation C108.2

**Continuous Air Barrier** Defined C202 Required C402.6.1

**Continuous Insulation (ci)**

Defined C202

Requirements C303.2.2, C402.1.3, Table C402.1.3, C402.2.2, C402.2.3

**Controls**

Capabilities C403.3.1, C403.4.1, C403.4.1.2, C403.4.2.1, C403.4.2.2,

C403.4.3.3.1, C403.4.5, C403.7.1, C404.6, C404.6.3

Chilled water plants C403.4.5 Economizers C403.5, C403.5.1,

C403.5.3.2, C403.5.3.3, Table C403.5.3.3

Energy recovery systems C403.7.4 Fan speed C403.11, C403.8, C403.8.6,

C403.8.6.1

Freeze protection system C403.14.4 Glazing C402.5.3.3

Heat pump C403.4.1.1, C403.4.3.3.1

Heating and cooling C403.3.1, C403.4, C403.5.1

Hot water system C404.6 Humidity C403.4.1, C403.5.1,

C403.7.4.2

HVAC C403.4, C408.2.3.2

Hydronic systems C403.4.3 Lighting C402.5, C402.5.1.1,

C402.5.1.2, C402.5.2.1, C402.5.3.1, C405.2, C405.5.1

Off hour C403.4.2

Service water heating C404.6 Shutoff dampers C403.7.7 Snow melt system C403.14.2

Temperature C403.4.1, C403.4.2, C403.4.2.1, C403.4.2.2, C403.4.2.3, C403.7.7

Three-pipe system C403.4.3.1 Two-pipe changeover system

C403.4.3.2

Variable air volume systems C403.5.2, C403.6

Ventilation C403.2.2

**Cooling Systems**

Hot gas bypass limitation C403.3.3 **Cooling Tower** C403.11.3, C403.11.4 **Cooling with Outdoor Air** C403.5.1 **Crawl Space Walls**

Defined C202 Requirements C303.2.1

**Curtain Wall**

Air leakage of fenestration Table C402.6.3

Defined C202

**Dampers** C402.6.5, C403.7.7

**Data Center** C202, C405.9

**Data Center Systems** C202, C403.1.2

**Daylight Responsive Control**

Defined C202

Required C402.5.1.1, C402.5.1.2, C402.5.2.1, C402.5.3.1, C402.5.3.2

**Daylight Zone** C402.5.1.1, C402.5.2, C405.2.4

Defined C202

**Daylight Zone Control** C405.2.4

**Deadband** C403.4.1.2, C403.4.1.4, C403.4.3.3.1

**Dedicated Outdoor Air System (DOAS)** C202, Table C403.3.2(12), Table C403.3.2(13)

**Degree Day Cooling (CDD)** Table C301.3 **Degree Day Heating (HDD)** Table C301.3 **Dehumidifier** C202, C403.15,

Table C403.3.2(11)

**Demand Control Kitchen Ventilation (DCKV)** C202, C403.7.5

**Demand Control Ventilation (DCV)**

Defined C202

Requirements C403.7.1, C409.6.1.10.3

**Demand Recirculation Water System**

Defined C202 Requirements C404.6.1.1

**Demand Response Signal** C202

**Demand Responsive Control** C202

**Desiccant Dehumidification System** C202, C403.15

**Design Conditions** C302

**Direct Digital Control (DDC)** C202, C403.6.8

**Direct Expansion (DX)** C403.8.6.1

**Doors**

Default *U*-factors Table C303.1.3(2) Garage doors C303.1.3

Loading docks C402.6.7 Opaque C303.1.3 Performance requirements

Table C402.1.2, Table C402.1.3, C402.5, C402.5.5, C402.6.3

Vestibules C402.6.6

**Drain Water Heat Recovery** C404.7

**Dual Duct VAV** C403.6.3, C403.6.4

**Duct** C202

**Duct System**

Defined C202 Requirements C403.13.2

**Ducts**

Defined C202

Insulation C105.2, C403.13.1, C403.13.2, C403.13.2.1, C403.13.2.2, C403.13.2.3

Sealing C105.2, C403.13.1, C403.13.2.1, C403.13.2.2, C403.13.2.3

**Dwelling Unit**

Defined C202 Electrical Meter C405.6 Lighting C405.1 Testing C402.6.2.2 Vestibules C402.6.6

**DX-Dedicated Outdoor Air System Units (DX- DOAS Units)** C202, C406.2.2.5

**Dynamic Glazing**

Defined C202 Requirements C402.5.3.3

**East-Oriented** C202, C402.3

**Economizer**

Air C403.5.3, Table C403.5(1)

Controls C403.5.1 Defined C202

Fault detection and diagnostics (FDD) C403.2.3

High-limit shutoff control C403.5.3.3, Table C403.5.3.3

Requirements C403.5.3, C403.5.4 Water C403.5.4

**Economizer, Air** C202

**Economizer, Water** C202

**Efficiency, Additional** C406 **Electrical Meters** C405.13.3, C405.6 **Electrical Motors** C405.8

**Electrical Power and Lighting** C405 **Electrical Transformers** C405.7 **Elevator Power** C405.10.1, C405.10.2 **Elevator Shafts** C402.6.4, C402.6.5 **Emittance** C202, C402.3, C402.4

**Enclosed Space**

Defined C202

Under skylights C402.5.2 **Energy Analysis** C202, C407 **Energy Cost**

Compliance performance C401.2 Defined C202

Performance basis C407.2 **Energy Efficiency Ratio (EER)** C406.2.2 **Energy Monitoring** C405.13, C406.2.4

**Energy Recovery, Series** C202, C403.7.4.2

**Energy Recovery Ratio, Series (SERR)**

C202, C406.2.2.5

**Energy Recovery Ventilation System**

Defined C202 Requirements C403.7.4

**Energy Simulation Tool**

Defined C202

Requirements/use C101.4.1, C407, C407.2, C407.5.1.1

**Energy Storage System (ESS)** C202 **Energy Use Intensity (EUI)** C202 **Enthalpy Recovery Ratio** C202, C403.7.4,

C406.2.2.5

**Entrance Door**

Air leakage Table C402.6.3 Defined C202

Thermal performance Table C402.5

**Envelope, Building Thermal**

Defined C202

**Envelope Design Methods** C402.1.3, C402.1.2, C402.1.4

**Equipment Buildings** C402.1.1.3

**Equipment Efficiencies** C105.2, C403.3.2, C403.5.1, C403.8.6, C404.2

**Equipment Performance Requirements**

C403.3.2

Boilers Table C403.3.2(6) Condensing units Table C403.3.2(10)

Economizer exception Table C403.5(2) Heat rejection equipment

Table C403.3.2(7)

Packaged terminal air conditioners and heat pump Table C403.3.2(4)

Unitary air conditioners and condensing units Table C403.3.2(1)

Unitary and applied heat pumps Table C403.3.2(2)

Warm air duct furnaces and unit heaters Table C403.3.2(5)

Warm air furnaces Table C403.3.2(5)

Warm air furnaces/air-conditioning units Table C403.3.2(5)

Water chilling packages, standard Table C403.3.2(3)

Water heating C404.2.1, Table C404.2

**Equipment Room** C202

**Escalators** C405.10.2

**Exempt Buildings** C402.1.1, C402.1.1.3

**Exhausts** C402.6.5

**Existing Buildings** Chapter 5

**Exit Signs** C405.3.1

**Exterior Lighting** C405.2.7, C405.5

**Exterior Wall** C202

Thermal performance C402, C402.2.2

**Exterior Wall Envelope** C202

**External Shading** Table C407.4.1(1)

**Fan, Embedded** C202, C403.8.3

**Fan Array** C202, C403.8.3

**Fan Brake Horsepower (BHP)** C403.8.2 Defined C202

**Fan Electrical Input Power** C202, Table C409.6.1.10.2(1)

**Fan Energy Index (FEI)** C202, C403.8.3

**Fan Nameplate Electrical Input Power**

C202, C403.8.2

**Fan Power Limitation**

Table C403.8.1(1), Table C403.8.1(2)

**Fan System** C202

**Fan System, Complex** C202

**Fan System, Exhaust/Relief** C202, C403.5.3.5

**Fan System, Return** C202

**Fan System, Single-Cabinet** C202

**Fan System, Transfer** C202 **Fan System Airflow** C202 **Fan System BHP**

Allowable C403.8.1 Defined C202

**Fan System Design Conditions** Allowable C403.8.1 Defined C202

**Fan System Electrical Input Power**

C202, C403.8.3

**Fan System Motor Nameplate HP**

C403.8.1

Defined C202

**Fault Detection & Diagnostics (FDD)**

Economizers C403.5.5

**Fault Detection and Diagnostics (FDD) System** C202, C403.2.3, C406.2.6.4

**Fees** C106

Refunds C106.6 Related fees C106.5

Schedule of permit fees C106.2

**Fenestration (see also Doors)**

C303.1.3, C402.5

Air leakage (infiltration) rate C402.6.3, Table C402.6.3

Defined C202

Maximum area C402.5.1, C402.5.1.2 Rating and labeling C303.1.3, C402.1.3 Skylights C402.5.1.2, C402.5.2,

C402.5.2.1, C402.5.2.2, C402.5.3, C502.3.2, C503.2.3

Solar heat gain (SHGC) Table C402.5, C402.5.3

Vertical C402.1, Table C402.5, C402.5.1.1, C402.5.3, C502.3.1, C503.2.2

**Fenestration Product, Field-Fabricated**

C202

Air leakage C402.6.3

**Fenestration Product, Site-Built**

Defined C202

***F*-Factor**

Assembly *U*-, *C*- or *F*-factor method C402.1.2, Table C402.1.2

Defined C202

**Financial Renewable Energy Power Purchase Agreement** C202, C405.15.2.1

**Floor Area, Net**

Defined C202

Fenestration increase C402.5.1.1

**Floors**

Slab on grade C402.2.4 Thermal properties C402.2.3

**Freeze Protection Systems** C403.14.4

**Furnace Efficiency** Table C403.3.2(5)

**General Lighting**

Additional lighting C405.3.2.2.1 Daylight controls C405.2.4 Defined C202

Interior lighting power C405.3.1

**General Purpose Electric Motors**

Defined C202

**Glazing Area**

Default fenestration *U*-factors Table C303.1.3(1)

Dynamic C402.5.3.3, C406.3.4

**Green Retail Tariff** C202, C405.15.2.1

**Greenhouse**

Building envelope C402.1.1 Defined C202

**Group R** C202

**Guestroom** C403.7.6

**Haze Factor** C402.5.2.2

**Heat Pump** C403.4.1.1, C403.4.3.3

**Heat Recovery**

Drain water C404.7 Economizer exemption C403.5 Kitchen exhaust C403.7.5 Service water C403.11.5

**Heat Rejection Equipment**

Table C403.3.2(7), C403.11

**Heat Trace Systems** C404.6.2

**Heat Trap**

Defined C202 Required C404.3

**Heated Slab**

Defined C202

Insulation Table C402.1.2, Table C402.1.3, C402.2.4

**Heating and Cooling Loads** C302.1, C403.1.1, C403.3.1, C403.3.2, C403.4.1.1

**Heating Outside a Building** C403.14.1

**High-Capacity Gas-Fired Water Heater** C202, C404.2.1

**High-Speed Door**

Air leakage Table C402.6.3 Defined C202

**Historic Building**

Compliance C501.5 Defined C202

**Horticultural Lighting** C202, C405.4

**Hot Gas Bypass** C403.3.3, Table C403.3.3

**Hot Water** C404.2, C404.6

Efficient delivery C404.5 Piping insulation C404.4 System controls C404.6

Humidistat

Defined C202 Requirements C403.4.8

**Humidistatic Controls** C202, C403.4.8.1

**HVAC Equipment**

Automatic setback and shutdown C403.4.2.2

Automatic start and stop capabilities C403.4.2.3

Increased efficiency C406.2.2 Performance requirements C403.3.2 Supply-air temperature reset C403.6.5 System map zones Table C407.4.1(2),

C407.4.2.1

**HVAC Systems** C402.4, C403, C403.7.6, C403.8, Table C407.4.1(1),

Table C407.4.1(2), C408.2.2

Manuals C408.3.2.2 Plan C408.2.1

Report C408.2.4, C408.2.5

**HVAC Total System Performance Ratio (HVAC TSPR)** C202, C409

**Hydronic Heat Pump Systems** C403.4.3.3

**Ice Melt Systems** C403.14.2

**Identification (Materials, Equipment and System)** C303.1

**IEC Design H Motor** C202, Table C405.8(2)

**IEC Design N Motor** C202, Table C405.8(1)

**Indirectly Conditioned Space (see Conditioned Space) Indoor Grow** C202, C403.15

**Infiltration (see Air Barrier)**

Defined C202

**Information Technology Equipment (ITE)**

C202

**Inspections** C107

Inspection agencies C107.4 **Insulated Siding** C303.1.4.1 **Insulation**

Continuous insulation C303.2.2, C402.1.3, Table C402.1.3, C402.2.1

Duct C403.13.1

Identification C303.1, C303.1.2 Installation C303.1.1, C303.1.1.1,

C303.1.2, C303.2

Mechanical system piping C403.13.3 Piping C404.4

Plenum C403.13.1 Product rating C303.1.4

Protection of exposed foundation C303.2.1

Protection of piping insulation C403.13.3.1

Radiant heating systems C402.2.6 Requirements C402.1.3,

Table C402.1.3, C402.2, C402.2.6

**Integrated HVAC System** C202, C403.15

**Integrated Part Load Value (IPLV)**

Defined C202

Requirements Table C403.3.2(3), Table C403.3.2(15), C403.3.2.1

**Interior Lighting Power** C405.3, C405.3.2 **Internal Curtain System** C202, C402.1.1.2 **Isolation Devices** C202, C403.2.1, C403.7.6.2

**Kitchen Exhaust** C403.7.5, Table C403.7.5

**Labeled**

Dampers C403.7.7 Defined C202

Fans C403.8.3

Glazing, skylights C402.1.5, C402.2.1.2, C402.5.3.3

HVAC equipment Table C403.3.2(3) Lighting C402.6.1.2.1, C403.4.7,

C405.3.1

Requirements C303.1.3, Table C403.3.2(3)

**Large-Diameter Ceiling Fan** C202, C403.9

**Lighting Power**

Additional lighting C405.3.2.2.1, C405.5.1

Design procedures C405.3.2, C405.3.2.1, C405.3.2.2

Exterior connected C405.5, C405.5.1, Table C405.5.2(1), Table C405.5.2(2)

Interior connected C405.3, C405.3.1, C405.3.2, Table C405.5.2(1), Table C405.5.2(2)

Reduced lighting power density C406.2.5.6

**Lighting Systems** C405, C406.3

Controls, exterior C405.2.6, C405.5.1, Table C405.5.2(1), Table C405.5.2(2)

Controls, interior C405.2.2, C405.3, C405.3.1, C405.3.2, Table C405.3.2(1), Table C405.3.2(2), C406.4

Daylight responsive C405.2.4, C405.2.4.1

Dwelling and sleeping units C405.1, C405.2.2, C405.2.4, C405.2.5, C405.3.1

Existing buildings C502.1, C502.3.6, C504.1, C503.1, C503.5

Light reduction C405.2.3.1 Occupant sensor controls C405.2.1,

C405.2.1.1, C405.2.1.2

Recessed C402.6.1.2.1 Retail display C405.3.2.2.1

Specific applications C405.2.5 Time switch controls C405.2.2,

C405.2.2.1

**Liner System (Ls)**

Defined C202

Insulation Table C402.1.3

**Listed**

Defined C202

Kitchen exhaust hoods C403.7.5 Skylights C402.2.1.2

**Loading Dock Weatherseals** C402.6.7

**Low Slope**

Defined C202

Roof solar reflectance C402.4 **Low-Energy Buildings** C402.1.1 **Low-Voltage Dry-Type Distribution**

**Transformer** C202, C405.7

**Luminaire**

Controls C405.2.2, C405.2.5 Sealed C402.6.1.2.1 Wattage C405.3.1, C405.5.1

**Luminaire-Level Lighting Controls** C202

**Maintenance**

General C501.1.1, C501.3

Owner responsibility C501.3

**Manual** C202

**Manuals** C101.4.1

**Mass** C402.1.2.1.4, C402.1.3.4

Floor Table C402.1.2, Table C402.1.3

Wall C402.2.2

**Materials and Equipment** C303

**Mechanical Systems and Equipment**

C403

Existing buildings C502.1, C502.3.3, C503.3, C504

**Mechanical Ventilation** C403.1, C403.2.2 **Meters, Electrical** C405.13.3, C405.6 **Motor Nameplate Horsepower** C403.8.2

Efficiency C405.8

**Moving Walks** C405.10.2

**Multifamily Residential Buildings** C407.4.2.3

**Multiple-Zone Systems** C403.6, C403.6.5

Nameplate Horsepower

Defined C202

**Nema Design A Motor** C202, Table C405.8(1)

**Nema Design B Motor** C202, Table C405.8(1) **Nema Design C Motor** C202, Table C405.8(2) **Net Floor Area (see Floor Area, Net) Networked Guestroom Control System**

C202, C403.7.6

**Nonconditioned Space**

Alterations C502.2

**Nonstandard Part Load Value (NPLV)**

C202, C403.3.2.1

**North-Oriented** C202, C405.2.4.1

**Occupancy**

Complex HVAC systems C403.6 Compliance C102.1, C101.4

Lighting power allowances C405.2.2, C405.3.2, Table C405.3.2(1), Table C405.3.2(2), C405.3.2.1

Mixed occupancies C102.1.1

**Occupant Sensor Control** Commissioning C408.3.1.1 Defined C202

Outdoor heating C403.14.1 Required C405.2.1, C405.2.1.1,

C405.2.1.2

**Occupied-Standby Mode** C202, C403.7.8.1

**Off-Hour, Controls** C403.4.2, C403.7.7, C405.2.2.1

**On-site Renewable Energy**

Defined C202

**Opaque Areas** C402.1, Table C402.1.3, Table C402.1.2

**Opaque Door** C202

**Opaque Doors**

Defined C202

Regulated Table C402.1.3, C402.1.2, C402.5.5

**Operating and Maintenance Manual**

C408.3.2.2

**Orientation**

Daylight Responsive controls C405.2.4.1

Fenestration Table C402.5 Thermostatic controls C403.4.1,

C403.4.2

**Owner** C202

**Packaged Terminal Air Conditioner (PTAC)**

Requirements Table C403.3.2(4)

**Packaged Terminal Heat Pump**

Requirements Table C403.3.2(4)

**Parking Area, Exterior** C202, C405.2.7.3, Table C405.5.2(2)

**Parking Area, Interior** C202, C405.2 **Parking Garage Lighting Control** C405.2.9 **Parking Garage Section** C202, C403.7.2 **Parking Garage Ventilation** C403.7.2 **Performance Analysis** C407

**Permit (see Fees)** C106.4

**Photosynthetic Photon Efficacy (PPE)**

C202, C405.4

**Physical Renewable Energy Power Purchase Agreement** C202, C405.15.2.1

**Pipe Insulation** C403.13.3, C404.4 **Plans and Specifications** C105 **Plenums**

Insulation and sealing C403.13.1

**Pools** C404.8

Controls C404.8.1, C404.8.2

Covers C404.8.3

Existing buildings C502.3.5 **Power Density** C405.3.2.1 **Powered Roof/Wall Ventilators**

Defined C202

Fan efficiency exemption C403.8.3

**Process Application** C202

**Proposed Design**

Defined C202 Requirements C407

**PSI-Factor (****-Factor)** C202, C402.1.4, Table

C402.1.4, Table C407.4.1(1)

**Public Lavatory** C404.5.1

**Pump Energy Index (PEI)** C202, C403.17

**Pumping Systems** C403.4.3.3, C404.6, C408.2.2.2

**Purchased Energy** C202

**Radiant Heating System** Defined C202 Insulation C402.2.6

**Readily Accessible**

Defined C202 **Ready Access (To)** C202 **Recooling** C403.6

**Referenced Standards** Chapter 6, C110 **Refrigerant Dew Point** C202 **Refrigerated Warehouse Cooler**

Defined C202 Requirements C403.12

**Refrigerated Warehouse Freezer** Defined C202 Requirements C403.12

**Refrigeration Equipment**

Performance C403.12, Table C403.12.1

**Refrigeration System, Low Temperature**

C202

**Refrigeration System, Medium Temperature** C202

**Registered Design Professional** Commissioning C408 Defined C202

**Reheating** C403.6.5, C403.11.5

**Renewable Energy Certificate (REC)**

C202, C405.15.3, C405.15.4

**Renewable Energy Investment Fund (REIF)** C202, C405.15.2.1

**Renewable Energy Resources** C202

**Repair**

Defined C202

Historic buildings C501.5 Requirements C501.4, C504

**Replacement Materials** C501.4 Replacement fenestration C503.2.2.1

**Reroofing**

Defined C202 **Reset Control** C403.6.5 **Residential Building**

Compliance C101.2, C102.1.1, C101.4

Defined C202

**Roof Assembly**

Air barriers C402.6.2.3.2 Defined C202

Fenestration C402.5.1, C402.5.1.2, C402.5.2, C405.2.4.3

Recover C503.1

Reflectance and emittance options Table C402.4

Repairs C504.2 Replacement C503.2.1

Requirements C303.1.1.1, C402.2.1 Solar reflectance and thermal

emittance C402.4

**Roof Recover**

Defined C202 Exemption C503.1

**Roof Repair**

Defined C202

**Roof Replacement**

Defined C202 Requirements C503.2.1

**Roof Ventilators (see Powered Roof/Wall Ventilators)**

**Rooftop Monitor**

Daylight zones C405.2.4.2 Defined C202

Skylights required C402.5.2

**Rooms with Fuel-Burning Appliances** C402.1.5

***R*-Value (Thermal Resistance)** C202

**Saturated Condensing Temperature**

Defined C202

Refrigeration systems C403.12.3.1

**Scope Of Code** C101.2

**Seasonal Energy Efficiency Ratio (SEER)**

Table C403.3.2(1),

Table C403.3.2(2), Table C403.3.2(8), Table C403.3.2(9)

**Sensible Energy Recovery Ratio** C202, C406.2.2.5

**Service Water Heating**

Defined C202

Drain water heat recovery C404.7 Efficiency C404.2.1, C404.5

Existing buildings C502.3.4, C503.4, C504.1

Requirements C403.11.5, C404, C404.2, C404.2.1, C404.5, C404.6, C404.7

**Setback Thermostat** C403.4.2, C403.4.2.1, C403.4.2.2

**Shading** C402.4, C402.5.3

**SHGC (see Solar Heat Gain Coefficient) Shutoff Dampers** C402.6.5, C403.7.7 **Simulated Building Performance**

C202, C407

**Simulation Tool (see Energy Simulation Tool)**

**Single Zone** C403.5

**Sizing**

Equipment and system C403.3.1

**Skylights** C402.1.4, C402.4,

Table C402.5, C402.5.3.1, C402.5.3.2

Additions C502.3.2

Air leakage (infiltration) Table C402.6.3

Alterations C503.2.3

Curb insulation C402.2.1.2 Defined (see Fenestration) C202 Haze factor C402.5.2.2

Lighting controls C402.5.2.1 Maximum area C402.5.1, C402.5.1.2 Minimum area C402.5.2

**Slab-Edge Insulation** C303.2.1, C402.2.4

**Sleeping Unit**

Defined C202

Lighting C405.1, C405.2.2, C405.2.4, C405.2.5

**Small Electric Motor**

Defined C202

Minimum efficiency C405.8

**Snow Melt and Ice System Controls**

C403.14.2

**Solar Heat Gain Coefficient (SHGC)** C105.2, Table C303.1.3(3), Table C402.5, C402.5.1.1, C402.5.3, C402.5.3.1

Defined C202

Dynamic glazing C402.5.3.3 Replacement products C503.2.2.1

**South-Oriented** C202, C402.3

**Spas** C404.8, C404.9

**Stairways** C402.6.5, C403.7.7, C405.2, C405.2.1.1, Table C405.3.2(2)

**Standard Reference Design** Defined C202 Requirements C407, Table

C407.4.1(1), Table C407.4.1(3)

**Standards, Referenced** Chapter 6, C110

**Steel Framing** Table C402.1.3, C402.1.2.1.6, Table C402.1.2.1.6

**Stop Work Order** C110 Authority C110.1 Emergencies C110.3 Failure to comply C110.4 Issuance C110.2

**Storefront**

Defined C202

Glazing Table C402.6.3 **Substantial Improvement** C202, C503.6 **Supply Air Temperature Reset Controls**

C403.6.5

**Suspended Ceilings** C402.1.2.1.2, C402.1.3.3

**Swimming Pools** C404.8

**Temperature Deadband** C403.4.3.3.1

**Testing Unit Enclosure Area** C202, C402.6.2.2

**Thermal Block** C202, C407.4.2, C409.6.1.1

**Thermal Conductance (see C-Factor) Thermal Bridge** C202, C402.7 **Thermal Distribution Efficiency (TDE)**

C202, C403.13.1

**Thermal Mass (see Mass) Thermal Resistance (see *R*-Value)**

**Thermal Transmittance (see *U*-Factor) Thermostat**

Defined C202

Pools and spa heaters C404.8.1 Requirements C403.4, C403.4.1,

C403.4.1.2, C403.4.1.4, C403.4.2, C403.6

Setback capabilities C403.4.2

**Time Switch Control**

Defined C202

Requirements C405.2.2, C405.2.2.1 **Townhouse (see Residential Buildings) Transformers, Electric** C405.7

***U*-Factor (Thermal Transmittance)** C202

**Variable Air Volume Systems (VAV)** C403.5.2, C403.6.1, C403.6.2, C403.6.3, C403.6.4, C403.6.6, C403.6.7, C403.6.9, Table C407.4.1(3)

**Variable Refrigerant Flow System**

Defined C202 **Vegetative Roof** C202, C402.4 **Ventilation** C403.2.2

Defined C202

Demand control ventilation (DCV) C403.7.1

Energy recovery system C403.7.4.2, C406.6

Parking garages C403.7.2

**Ventilation Air**

Defined C202

Energy recovery C403.7.4.2 Fan controls C403.8.6.1 Kitchen exhaust C403.7.5

**Vertical Fenestration (see Fenestration) Vestibules** C402.6.6, C403.4.1.5

**Visible Transmittance (VT)**

Default glazed fenestration Table C303.1.3(3)

Defined C202

Dynamic glazing C402.5.3.3 Increased fenestration C402.5.1.1 Skylights C402.5.2, C405.2.4.3

**Visible Transmittance, Annual (VT Annual)**

C202, C402.5.1.1

**Voltage Drop** C202

**Walk-In Cooler**

Defined C202 Requirements C403.12,

Table C403.12.2.1(1), Table C403.12.2.1(2), Table C403.12.2.1(3)

**Walk-in Freezer**

Defined C202 Requirements C403.12

**Wall**

Above-grade wall, defined C202 Below-grade wall, defined C202 Crawl space wall, defined C202 Exterior wall, defined C202 Steel framed C402.1.2.1.6,

Table C402.1.2.1.6

Thermal resistance Table C402.1.3, Table C402.1.2, C402.2.2

**Wall, Above-Grade** C202

**Wall, Below-Grade** C202

**Wall Ventilators (see Powered Roof/Wall Ventilators)**

**Walls (see Exterior Walls and Envelope, Building Thermal)**

**Walls Adjacent to Unconditioned Space (see Building Thermal Envelope)**

**Water Economizer** C403.5, C403.5.4, C403.5.4.1, C403.5.4.2

**Water Heater**

Defined C202

Efficiency Table C404.2, C404.2.1 **Water Heating** C404, Table C404.2 **West-Oriented** C202, C402.3

**Window Area**

**(see Fenestration and Glazing Area) Work Area** C202

**Zone (see also Climate Zones)**

Defined C202

Requirements C403.4, C403.5, C407.4.2.1, C407.4.2.2

RESOURCES

**CRA**

### ALL-ELECTRIC COMMERCIAL BUILDING PROVISIONS

*Resources are related information that is not part of the code.*

**User notes:**

***About this resource:*** *This resource provides code compliance pathways for commercial buildings intended to result in all-electric buildings for adopting jurisdictions or individual projects.*

***ICC Council Policy-49 Note:*** *In considering whether to adopt the content in this resource, jurisdictions in the United States should note that federal law might be found to preempt the provisions it prescribes. See the Public Health and Welfare Act, 42 U.S.C. § 6297: Effect on other law. Whether the content of this resource or a modification thereof is subject to preemption may depend on court decisions or whether a waiver has been issued by the US Department of Energy pursuant to 42 U.S.C. § 6297(d).*

SECTION CRA101—GENERAL

**CRA101.1 Intent.** The intent of this resource is to amend the *International Energy Conservation Code* to reduce greenhouse gas emissions from *buildings* and improve the safety and health for *commercial building* occupants by requiring new *all-electric buildings* and efficient electrification of *existing buildings*.

**CRA101.2 Scope.** The provisions in this resource are applicable to *commercial buildings*. New construction shall comply with Section CRA103. *Additions, alterations, repairs* and *changes of occupancy* to *existing buildings* shall comply with Chapter 5 and Section CRA104.

SECTION CRA102—DEFINITIONS

**ALL-ELECTRIC BUILDING.** A *building* using no *purchased energy* other than electricity when utility power is available.

**APPLIANCE.** A device or apparatus that is manufactured and designed to utilize energy and for which this code provides specific requirements.

**COMBUSTION EQUIPMENT.** Any equipment or appliance used for space heating, *service water heating*, cooking, clothes drying, humidification or lighting that uses fuel gas or fuel oil.

**PURCHASED ENERGY.** Energy or power purchased for consumption and delivered to the building site.

**SUBSTANTIAL IMPROVEMENT.** Any repair, reconstruction, rehabilitation, alteration, *addition* or other improvement of a building or structure, the cost of which is equal to or greater than 50 percent of the market value of the structure before the improvement. Where the structure has sustained substantial damage as defined in the *International Building Code*, any repairs are considered substantial improvement regardless of the actual repair work performed. Substantial improvement does not include the following:

1. Improvement of a building required to correct health, sanitary or safety code violations ordered by the code official.
2. Alteration of a historic building where the alteration will not affect the building’s designation as a historic building.

SECTION CRA103—NEW COMMERCIAL BUILDINGS

**CRA103.1 Application.** New *commercial buildings* shall be all-electric buildings and comply with Section C401.2.1 or C401.2.2.

1. *Purchased energy* other than electricity shall be permitted where it has been demonstrated to the *code official* that the *building* is required by an applicable law or regulation to provide space heating with an emergency power system or a standby power system.
2. *Purchased energy* shall be permitted for an emergency power system or a standby power system.

**CRA103.2 Electric resistance heating equipment.** The sole use of electric resistance equipment and *appliances* for space and water heating shall be prohibited other than for *buildings* or portions of *buildings* that comply with not less than one of Sections CRA103.2.1 through CRA103.2.8.

**CRA103.2.1 Low space heating capacity.** Electric resistance *appliances* or equipment shall be permitted in *buildings* or areas of *buildings* not served by a mechanical cooling system and with a total space heating capacity not greater than 4.0 Btu/h (1.2 watts) per square foot of *conditioned space*.

**CRA103.2.2 Small systems.** *Buildings* in which electric resistance *appliances* or equipment comprise less than 5 percent of the total system heating capacity or serve less than 5 percent of the *conditioned floor area*.

**CRA103.2.3 Specific conditions.** Portions of *buildings* or specific equipment and *appliances,* subject to approval, that require electric resistance heating and cannot practicably be served by electric heat pumps.

**CRA103.2.4 Kitchen makeup air.** Makeup air for commercial kitchen exhaust systems required to be tempered by Section

* + 1. of the *International Mechanical Code* is permitted to be heated by electric resistance.

**CRA103.2.5 Freeze protection.** The use of electric resistance heat for freeze protection shall comply with Sections CRA103.2.5.1 and CRA103.2.5.2.

**CRA103.2.5.1 Low indoor design conditions.** Space heating systems sized for spaces with indoor design conditions of not greater than 40°F (4.5°C) and intended for freeze protection, including temporary systems in unfinished spaces, shall be permitted to use electric resistance. The *building thermal envelope* of any such space shall be insulated in accordance with Section C402.1.

**CRA103.2.5.2 Freeze protection system.** Freeze protection systems shall comply with Section C403.14.4.

**CRA103.2.6 Preheating of outdoor air.** Hydronic systems without energy recovery ventilation and that do not use freeze protec- tion fluids shall be permitted to utilize electric resistance to temper air to not more than 40°F (4.5°C). All systems with energy recovery ventilation shall be permitted to utilize electric resistance to preheat outdoor air to defrost or temper air entering the energy recovery device and shall comply with one of the following:

* + - 1. Where the space is mechanically humidified or has a *process application* that will maintain the space above 30 percent relative humidity when the outdoor temperature is not greater than 25°F (-4°C) and the system recovers latent energy, the outdoor air shall not be preheated to greater than 25°F (-4°C).
      2. For sensible-only heat recovery exchangers, outdoor air shall not be preheated to greater than 25°F (-4°C).
      3. For all other systems, outdoor air shall not be preheated to greater than 5°F (-15°C).

**CRA103.2.7 Small buildings.** *Buildings* with a *conditioned floor area* of not more than 250 square feet (23.2 m2) and not served by a mechanical space cooling system shall be permitted to use electric resistance *appliances* or equipment for space heating.

**CRA103.2.8 Supplemental heat.** Electric resistance heat shall be permitted as supplemental heat where installed with heat pumps sized in accordance with Section CRA103.3 and where operated only when a heat pump cannot provide the necessary heating energy to satisfy the *thermostat* setting.

**CRA103.3 Heat pump sizing for space heating.** Heat pump space heating systems shall be sized to meet the building heating load at the greater of 0°F (-18°C) or the 99 percent annual heating dry-bulb for the nearest weather station provided in the ASHRAE *Hand- book of Fundamentals*. The heat pump space heating system shall not require the use of supplemental electric heat at or above this temperature other than for defrosting. Lower capacity heat pumps that operate in conjunction with thermal storage shall be permit- ted if the system meets the requirements of this section.

**CRA103.4 Heat pump sizing for water heating.** Heat pump *service heating systems* shall be sized to meet not less than the *building service water heating* load at the greater of 15°F (-9.5°C) or the 99 percent annual heating dry-bulb for the nearest weather station provided in the latest edition of the ASHRAE *Handbook of Fundamentals*. Supplemental electric heat shall not be required at or above this temperature other than for temperature maintenance in recirculating systems and defrosting.

**CRA103.5 Heating outside a building.** Systems for heating outside a *building* shall comply with Section C403.14.1.

**CRA103.6 Low capacity cooling equipment.** Air conditioners with capacities less than 240,000 Btu/h (70 kW) shall be electric heat pump equipment sized and configured to provide both space cooling and space heating.

SECTION CRA104—EXISTING COMMERCIAL BUILDINGS

**CRA104.1 Combustion equipment in additions.** *Additions* shall use no *purchased energy* other than electricity and new equipment installed to serve additions shall not use *purchased energy* other than electricity. Where existing systems using *purchased energy* other than electricity serve an *addition,* the *existing building* and *addition* together shall not use more *purchased energy* other than electricity than the *existing building* alone.

**CRA104.2 Substantial improvement.** Buildings undergoing *substantial improvements* shall be all-electric buildings, comply with Section C402.5 and meet a site EUI by building type in accordance with ASHRAE Standard 100 Table 7-2a.

**Exception:** Compliance with ASHRAE Standard 100 shall not be required where *Group R* occupancies achieve an ERI score of 80 or below without *on-site renewable energy* included, in accordance with ANSI/RESNET/ICC 301, for each *dwelling unit*.

**CRA104.3 Cooling equipment.** New and replacement air conditioners shall be electric heat pump equipment sized and configured to provide both space cooling and space heating. Any existing space heating systems, other than existing heat pump equipment, that serve the same *zone* as the new equipment shall be configured as supplementary heat in accordance with Section CRA104.6.

**CRA104.4 Service water heating equipment.** Where *water heaters* are added or replaced, they shall not use *purchased energy* other than electricity.

**CRA104.5 Furnace replacement.** Newly installed warm air furnaces provided for space heating shall be permitted only as supple- mentary heat controlled in accordance with Section CRA104.6.

**CRA104.6 Heat pump supplementary heat.** Heat pumps having combustion equipment or electric resistance equipment for supplementary space or *service water heating* shall have controls that limit supplemental heat operation to only those times when one of the following applies:

1. The heat pump is operating in defrost mode.
2. The vapor compression cycle malfunctions.
3. For space heating systems, the *thermostat* malfunctions.
4. For space heating systems, the vapor compression cycle cannot provide the necessary heating energy to satisfy the *thermo- stat* setting.
5. The outdoor air temperature is less than the design temperature determined in accordance with Section CRA103.3.

**RESOURCE CRA—ALL-ELECTRIC COMMERCIAL BUILDING PROVISIONS**

1. For *service water heating*, the heat pump water heater cannot maintain an output water temperature of 120°F (49°C).
2. For temperature maintenance in *service water heating* systems.

New supplementary space and *service water heating* systems for heat pump equipment shall not be permitted to have a heating output capacity greater than the heating output capacity of the heat pump equipment.

SECTION CRA105—REFERENCED STANDARDS

**CRA105.1 General.** See Table CRA105.1 for standards that are referenced in various sections of this resource. Standards are listed by the standard identification with the effective date, the standard title, and the section or sections of this resource that reference this standard.

|  |  |  |
| --- | --- | --- |
| **TABLE CRA105.1—REFERENCED STANDARDS** | | |
| **STANDARD ACRONYM** | **STANDARD NAME** | **SECTION HEREIN REFERENCED** |
| ASHRAE 100—2018 | *Energy Efficiency in Existing Buildings* | CRA104.2 |
| ASHRAE—2017 | *2017 ASHRAE Handbook of Fundamentals* | CRA103.3 |
| ANSI/RESNET/ICC 301—2022 | *Standard for the Calculation and Labeling of Energy Performance of Dwelling and Sleeping Units using an Energy Rating Index* —includes Addendum A, Approved July 28, 2022, and Addendum B, Approved October 12, 2022 | CRA104.2 |

RESOURCE

**CRB**

### THE 2030 GLIDE PATH (PRESCRIPTIVE)

*Resources are related information that is not part of the code.*

**User notes:**

***About this resource:*** *This resource is intended to be adopted by jurisdictions that will require new construction to operate at net zero energy by the year 2030. It reduces the net annual energy use of buildings by approximately one-third in comparison with buildings constructed in compliance with the* 2021 IECC*. It is assumed that the 2027 and 2030 editions will also reduce energy use by one- third each.*

***ICC Council Policy-49 Note:*** *This resource is an accompaniment to the performance pathway included within Appendix CD and is intended for adopting authorities that wish to extend beyond the mandatory provisions of this code toward Zero Net Energy goals. For jurisdictions in the United States, compliance options for this prescriptive path may be limited if using only minimum efficiency mechanical and service water heating equipment. Adopting authorities may need to consider alternative means to expand methods for compliance under these conditions (see Section C104.1). Adopting authorities should be aware of potential preemption issues based on the Energy Policy and Conservation Act when evaluating whether to adopt the content in this resource. See the Public Health and Welfare Act, 42 U.S.C. § 6297: Effect on other law. Whether the content in this resource or a modification thereof is subject to preemption may depend on court decisions or whether a waiver has been issued by the US Department of Energy pursuant to 42 U.S.C. § 6297(d).*

SECTION CRB101—COMPLIANCE

**CRB101.1 Prescriptive compliance.** Where compliance is demonstrated using the Prescriptive Compliance option in Section C401.2.1, the number of additional efficiency credits required by Section C406.1 shall be 1.4 times the number that is required by Section C406.1.1.

**Exception:** Where a building achieves more renewable and load management credits in Section C406.3 than are required in Section C406.1.2, surplus credits shall be permitted to reduce required energy efficiency cred- its as follows:

*EECred* = *EECtbl* - {the lesser of: [*SRLMlim*, *SLRMadj* × (*RLMach* - *RLMreq*)]} where:

*EECred* = Reduced required energy efficiency credits.

*EECtbl* = Required energy efficiency credits from Table C406.1.1(1).

*SRLMlim* = Surplus renewable and load management credit limit from Table CRB101.1.

*SRLMadj* = 1.0 for all-electric or all-renewable buildings (excluding emergency generation); 0.7 for buildings with fossil fuel equipment (excluding emergency generation).

*RLMach* = Achieved renewable and load management credits from Section C406.3.

*RLMreq* = Required renewable and load management credits from Section C406.1.2.

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TABLE CRB101.1—LIMIT TO ENERGY EFFICIENCY CREDIT CARRYOVER FROM RENEWABLE AND LOAD MANAGEMENT CREDITS** | | | | | | | | | | | | | | | | | | | |
| **BUILDING OCCUPANCY GROUP** | **CLIMATE ZONE** | | | | | | | | | | | | | | | | | | |
| 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8 |
| R-2, R-4 and I-1 | 19 | 25 | 27 | 29 | 33 | 20 | 15 | 37 | 36 | 5 | 37 | 34 | 5 | 8 | 36 | 5 | 5 | 5 | 5 |
| I-2 | 17 | 13 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 7 | 16 | 20 | 15 | 21 | 20 | 43 |
| R-1 | 9 | 5 | 9 | 5 | 22 | 7 | 13 | 23 | 25 | 5 | 22 | 19 | 5 | 18 | 16 | 5 | 5 | 5 | 6 |
| B | 5 | 5 | 5 | 5 | 6 | 6 | 5 | 9 | 13 | 10 | 26 | 20 | 9 | 25 | 34 | 5 | 9 | 9 | 32 |
| A-2 | 31 | 28 | 25 | 26 | 23 | 16 | 5 | 8 | 16 | 5 | 8 | 7 | 5 | 5 | 9 | 5 | 5 | 5 | 5 |
| M | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |
| E | 17 | 15 | 23 | 16 | 20 | 14 | 5 | 22 | 27 | 10 | 32 | 16 | 10 | 21 | 12 | 5 | 5 | 15 | 10 |
| S-1 and S-2 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |
| All other | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |